## Overview and Purpose
VarStec Power Solutions, LLC
PO Box 942
|  |  | Saratoga Springs, NY 12866 | MotorVAR Medium-Voltage Motor Starting System
518.369.7589
MotorVAR™ Medium-Voltage Motor Starting System Overview and Purpose of This Workbook
| Info@VarStec.com |  |  |  | Info@VarStec.com | 2 ¦ P a g e
Sheet Rev Date: 1-11-2026
0 |  |  |  | 0
| Info@VarStec.com |  | 3 ¦ P a g e |  | Info@VarStec.com | 4 ¦ P a g e
| Info@VarStec.com |  | 5 ¦ P a g e |  | Info@VarStec.com | 6 ¦ P a g e
| Info@VarStec.com |  | 7 ¦ P a g e |  | Info@VarStec.com | 8 ¦ P a g e
Overview
VarStec’s MotorVAR™ is a medium-voltage motor starting capacitor bank designed to enable the reliable starting of large induction and synchronous motors while maintaining acceptable system and motor terminal voltages. By supplying reactive power locally during motor acceleration, MotorVAR minimizes voltage sags caused by inrush current and reduces reactive power flow across the electrical network. This allows motors to be started across the line at full voltage, preserving starting torque while supporting grid stability.
Compared to traditional starting methods, such as line reactors, Reduced-Voltage Soft Starters (RVSS), and Adjustable Speed Drives (ASD/VFDs)—MotorVAR provides a simpler, more robust, and more cost-effective solution. Reactor and RVSS systems limit inrush current by reducing motor voltage, often constraining available starting torque. In applications where these methods cannot meet torque requirements, MotorVAR can provide supplemental voltage support, extending their effective range and avoiding the cost and complexity of VFD drives.
MotorVAR introduces no steady-state harmonics, requires no climate-controlled E-House, and does not rely on proprietary power electronics or software. The system is designed for outdoor substation installation, eliminating the footprint and operating costs associated with E-Houses. MotorVAR also eliminates the need for synchronous bypass switchgear and complex transfer schemes, simplifying system design and commissioning.
Built entirely from proven, off-the-shelf components, MotorVAR employs a fully transparent, non-proprietary protection and control architecture. As a result, routine maintenance and troubleshooting can be performed by qualified plant personnel, reducing lifecycle cost and improving long-term reliability.
Workbook Purpose
This workbook is intended to support the preliminary evaluation and comparison of large medium-voltage motor starting configurations using VarStec’s MotorVAR system. It provides a structured framework for assessing voltage performance, starting torque margins, and reactive power requirements across several commonly encountered system topologies. Each worksheet represents a distinct starting configuration and is used to identify appropriate MotorVAR and auxiliary equipment ratings that meet defined system performance objectives during motor starting.
DOL + MotorVAR This worksheet evaluates across-the-line motor starting with MotorVAR providing reactive power support. The MotorVAR reactive power rating is iterated to meet system voltage and motor terminal voltage performance objectives while preserving full starting torque. This configuration is typical of gas compression stations, pump stations, and similar installations where large motors must be started directly on weak or utility-constrained power systems.
DOL + MotorVAR + RVSS This worksheet evaluates systems using a Reduced-Voltage Soft Starter (RVSS in combination with MotorVAR. Both the MotorVAR reactive power rating and RVSS current-limit setting are iterated to optimize voltage performance and starting torque. In many applications, MotorVAR significantly extends the practical operating range of RVSS systems, enabling higher horsepower motors to be started without resorting to complex and expensive VFD drives.
This configuration also accounts for the harmonic content produced by RVSS systems. Where required, capacitor detuning is incorporated into the MotorVAR design to avoid resonance, which can increase overall system cost. A common application addressed by this worksheet is the retrofit scenario in which an RVSS has already been installed but cannot be set to a sufficiently high current limit due to system weakness. In such cases, MotorVAR provides a practical and cost-effective means of restoring acceptable starting performance and making use of existing RVSS equipment.
DOL + MotorVAR + Reactor This worksheet evaluates a combined solution using both a line reactor and MotorVAR. The reactor impedance and MotorVAR reactive power rating are iterated together to achieve acceptable voltage performance while controlling inrush current. The reactor reduces required MotorVAR size but at the expense of motor terminal voltage and available starting torque. The tool is used to identify an optimal balance between reactor impedance and MotorVAR rating that satisfies overall system performance objectives without unnecessarily oversizing either component.
DOL + MotorVAR + Captive Transformer This worksheet evaluates systems incorporating a captive or dedicated transformer supplying the motor bus. In this configuration, the captive transformer introduces additional impedance into the network that must be explicitly accounted for during motor starting. In addition, multiple system voltage levels must be evaluated for performance, including the motor terminal voltage, the internal plant distribution voltages on the secondary of the captive transformer, the secondary of the upstream step-down transformer, and the voltage at the point of common coupling (PCC).
In this worksheet, the MotorVAR reactive power rating is iterated to simultaneously meet voltage performance objectives across multiple plant voltage levels, the PCC, and the motor terminals during starting. This configuration is typical of very large industrial plants and facilities that distribute power at more than one medium-voltage level, where transformer impedance and internal voltage regulation play a critical role in overall motor starting performance.

## DOL - MotorVAR
VarStec Power Solutions, LLC
PO Box 942
[18 empty] | Saratoga Springs, NY 12866 | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION
[18 empty] | 518.369.7589 | [12 empty] | Unassisted Motor Start Results | [17 empty] | Assisted Motor Start Results
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION | [36 empty] | Starting Current: | 184.993193447452-1044.75462461792i | [13 empty] | Starting Current as seen by system: | 296.949624875633-160.990496170873i
[19 empty] | 📜 Motor Starting Performance Summary | [17 empty] | Starting Current: | 1061.0065 |  |  | < | -79.9588 |  | amps | [7 empty] | Starting Current as seen by system: | 337.7825 | < | -28.4642 | amps
📜 Project Details | [16 empty] | April 13, 2026 | [6 empty] | Unassisted Motor Start |  |  |  | MotorVAR-Assisted Motor Start | [8 empty] | Percent of Motor FLA: | 301.5% | [13 empty] | Starting Current as seen by system (% of FLA): | 95.99%
[19 empty] | Parameter | [17 empty] | Percent of Rated Torque: | 36.36% | [13 empty] | Motor Current: | 157.756235523008-1549.61988251571i
|  | Project: | Name | [8 empty] | VarStec Ref: | VarStec Reference | [9 empty] | Starting Current (Magnitude and Angle): | 1061 amps, -79.96° |  |  |  | 1557.6 amps, -84.19° | [8 empty] | Voltage at motor terminals: | 7957.09753942553-207.774174178197i | [13 empty] | Motor Current: | 1557.6292 | < | -84.1871 |  | amps
|  | Customer: | Name | [8 empty] | Revision #: | Rev 1 | [9 empty] | Starting Current (% of FLA): | 301.5% |  |  |  | 442.6% | [8 empty] | Voltage at motor terminals: | 7959.8098 |  |  | < | -1.4958 |  | Volts | [7 empty] | Percent of Motor FLA: | 442.6%
[23 empty] | Motor Terminal Voltage at Start: | 7.96 kV |  |  |  | 11.69 kV | [8 empty] | Percent of motor voltage rating: | 60.3% | [13 empty] | Percent of Full Torque: | 78.37%
🧮 Purpose of Spreadsheet Tool | [22 empty] | Motor Terminal Voltage (% of Rating): | 60.3% |  |  |  | 88.53% | [8 empty] | Percent Voltage at Motor Bus: | 63.83% | [13 empty] | Voltage at motor terminals: | 11627.2715777426-1165.49408772741i
[23 empty] | Percent of Rated Starting Torque: | 36.36% |  |  |  | 78.37% | [8 empty] | Percent voltage Sag at Motor Bus: | 36.17% | [13 empty] | Voltage at motor terminals: | 11685.539 | < | -5.7241 | Volts
[37 empty] | Step-Down Transformer Ratio: | 2.7666 | [13 empty] | Percent of motor voltage rating: | 88.53%
[37 empty] | Voltage at Primary: | 23480.5072829916-367.691482396144i | [13 empty] | Percent Voltage at Motor Bus: | 93.71%
[19 empty] | 📜 System Impact Summary | [17 empty] | Voltage at Primary: | 23483.386 |  |  | < | -0.89715 |  | Volts | [7 empty] | Percent voltage Sag at Motor Bus: | 6.291%
🧮 System Data | [23 empty] | Unassisted Motor Start |  |  |  | MotorVAR-Assisted Motor Start | [8 empty] | Percent of Primary Voltage Rating: | 68.07% | [13 empty] | Step-Down Transformer Ratio: | 2.7666
[19 empty] | Parameter | [17 empty] | Percent voltage sag at primary bus: | 31.93% | [13 empty] | Voltage at Primary: | 32407.4562822558-2818.19543907465i
Utility Source (PCC) | [8 empty] | System Configuration | [13 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | 23.48 kV |  |  |  | 32.53 kV | [23 empty] | Voltage at Primary: | 32529.7625 | < | -4.97 | Volts
|  |  |  | (Source Voltage): | 34.5 |  | kVLL | [15 empty] | Percent of Nominal: | 68.07% |  |  |  | 94.29% | [23 empty] | Percent of Primary Voltage Rating: | 94.29%
|  |  |  | Short Circuit Current at Primary Vp: | 1.2 |  | kA3-phase | [15 empty] | Voltage Drop: | 31.93% |  |  |  | 5.711% |  |  |  | Utility Impedance at Motor Bus Voltage | [19 empty] | Percent voltage sag at primary bus: | 5.711%
|  |  |  | X/R Ratio: | 7 | [26 empty] | R | 0.30704 |  | ohms |  |  | 2.1711 |  |  | < | 81.8699 |  | ohms
Step-Down Transformer | [22 empty] | Voltage at Secondary 12.47 kV Bus: | 7.96 kV |  |  |  | 11.69 kV |  |  |  | X | 2.1493 |  | ohms | [15 empty] | MotorVAR Current: |  |  |  | 1395.5882
|  |  |  | Base MVA Rating: | 40 |  | MVA | [15 empty] | Percent of Nominal: | 63.83% |  |  |  | 93.71% |  |  |  | 0.307044597667228+2.1493121836706i | [7 empty] | ohms
|  |  |  | Secondary Voltage VS: | 12.47 |  | kVLL | [15 empty] | Voltage Drop: | 36.17% |  |  |  | 6.291% |  |  |  | Step-Down Transformer Impedance at Motor Bus Voltage
|  |  |  | Leakage Impeadance of Transformer: | 7.5 |  | % | [24 empty] | R | 0.010171 |  | ohms |  |  | 0.29156 |  |  | < | 88.001 |  | ohms
|  |  |  | X/R Ratio: | 28.65 | [17 empty] | Starting Current Seen by 34.5 kV System: | 384 amps |  |  |  | 122 amps |  |  |  | X | 0.29139 |  | ohms
Motor | [10 empty] | 34.5kV Bus |  |  |  |  | Isc: 1.2kA | [6 empty] | Percent of Motor FLA at 34.5 kV: | 301.5% |  |  |  | 95.99% |  |  |  | 0.0101705670059812+0.291386744721362i | [7 empty] | ohms
|  |  |  | Voltage Rating: | 13.2 |  | kVLL | [8 empty] | X/R: 7 | [15 empty] | Locked Rotor Motor Impedance at Motor Voltage
|  |  |  | Horse Power Rating: | 9923 |  | HP | [6 empty] | 40 MVA | [8 empty] | Starting Current Seen by 12.47 kV System: | 1061 amps |  |  |  | 338 amps |  |  |  | R | 0.8673 |  | ohms |  |  | 4.3365 |  |  | < | 78.463 |  | ohms
|  |  |  | Full Load Current Rating (FLA): | 351.9 |  | amps | [6 empty] | 7.5% | [8 empty] | Percent of Motor FLA at 12.47 kV: | 301.5% |  |  |  | 95.99% |  |  |  | X | 4.2489 |  | ohms
|  |  |  | Full Load Power Factor: | 90 |  | % |  |  | 12.47kV Bus | [21 empty] | 0.867298414716478+4.24887714156024i | [7 empty] | ohms
|  |  |  | Full Load Efficiency: | 97.4 |  | % | [11 empty] | Voltage change per stage at the 12.47 kV Bus: | [8 empty] | ±7.12% |  |  |  | MotorVAR Impedance at MotorVAR Voltage Rating
|  |  |  | Locked Rotor Current Rating (LRA): | 500 |  | % | [7 empty] | 9,923 HP Motor | [16 empty] | R | 0 |  |  | ohms
|  |  |  | Locked Rotor Power Factor (PF): | 20 |  | % | [8 empty] | FLA: 351.9A |  |  | Table Summary | [12 empty] | X | -4.84 |  |  | ohms |  |  |  | ohms
MotorVAR | [15 empty] | LRA: 500% |  |  | The MotorVar reduces the 12.47kV system's inrush current from 1061 amps (302 %FLA) to 338 amps amps (96 % of FLA). As a result, the 12.47 kV busimproves from 63.8% to 93.7% of nominal, while the 34.5 kV primary voltage improves from 68.1% to 94.3% of nominal during motor starting. The higher motor terminal voltage increased available starting torqe from 36.4% to 78.4%. | [12 empty] | -4.84i | [7 empty] | ohms
|  |  |  | MotorVAR Voltage Rating: | 13.2 |  | kVLL | [24 empty] | Total Impedance at Motor Voltage (unassisted)
|  |  |  | MotorVAR Reactive Power Rating: | 36 |  | MVAR | [24 empty] | 1.18451357938969+6.6895760699522i | [7 empty] | ohms
|  |  |  | Number of Stages: | 4 | [31 empty] | Total Impedance at Motor | 6.7936 |  |  | < | 79.9588 |  | ohms
[19 empty] | Note: | [12 empty] | Impedance of Motor and MotorVAR System
[19 empty] | This analysis provides preliminary MotorVAR sizing intended for feasibility assessment and system impact evaluation. Final MotorVAR configuration, staging, and protection coordination should be confirmed with a detailed engineering and dynamic motor starting study. | [12 empty] | 18.4426119342146+7.72989439697291i | [8 empty] | 19.997 |  |  | < | 22.7401 | ohms
[8 empty] | 13.2KV, 36 MVAR | [23 empty] | Total Impedance at Motor Voltage (assisted)
[8 empty] | 4 Stage MotorVAR | [23 empty] | 18.7598270988878+10.1705933253649i
[6 empty] | ` | [30 empty] | Total Impedance at Motor | 21.3394 |  |  | < | 28.4642 |  | ohms
| Info@VarStec.com | [18 empty] | Info@VarStec.com | [9 empty] | 2 ¦ P a g e |  |  | Short Circuit Current at secondary bus: | [7 empty] | 0.377460113665694-2.90423219798979i | [5 empty] | kA
[13 empty] | Sheet Rev Date: 1-11-2026 | [27 empty] | 2.9287 |  |  | kA
[39 empty] | MVA short circuit: |  | 63.1802 |  |  | MVAsc
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION | [18 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION
🧮 Summary of Input Data | [18 empty] | 🧮 One-Line Representation of Results | [15 empty] | Text Box 1
Based on the data provided, this analysis evaluates the starting performance of a 9,923 HP, 13.2 kV motor connected to a utility system with a 34.5 kV point of common coupling (PCC). The utility short-circuit level at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, supplying the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 351.9 amps, a locked-rotor current (LRA) of 500% FLA, and a rated efficiency of 97.4% and power factor of 90%. To support motor starting, a MotorVAR system rated at 36 MVAR at 13.2kV, configured in 4 stages, is applied at the motor bus.
Text Box 2
Without MotorVAR assistance, the motor draws 1061 amps (301.5% of FLA) during starting. This results in a voltage drop, with the motor terminal voltage dropping to 7.96 kV, or 60.3% of rated voltage. Correspondingly, available starting torque drops to 36.4% of rated torque, increasing the risk of stalled or prolonged motor acceleration. From a system perspective, the voltage at the 34.5 kV PCC drops to 23.48 kV, or 68.1% of rated voltage and the 12.47 kV Secondary bus drops to 7.96 kV or 63.8% of nominal voltage, or voltage drops of 31.9% and 36.2% respectively. Typical performance objectives call for a voltage of no lower than 90% of nominal at the secondary bus and 96% voltage at the primary. When these objectives are not met, alternative starting methods are typically evaluated.
Text Box 3
With the MotorVAR system engaged, motor starting performance improves substantially. Starting current at the motor terminals is increased to 1558 amps while the current drawn through the 12.47kV system is reduced to 338 amps (96% of FLA), while motor terminal voltage is maintained at near 11.7 kV, or 88.5% of rated voltage. This enables the motor to develop approximately 78.4% of rated torque at starting, providing stronger acceleration and more stable operation. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5 kV bus remain at approximately 94.3% and 93.7% of nominal, respectively. The starting current seen by the 34.5 kV and 12.5 kV system are reduced to approximately 96 %FLA respective of the voltage levels, greatly mitigating upstream system disturbances. As the system pulls into synchronism, the 4 stage MotorVAR system limits the voltage fluctuations to approximately ±7.12%% of the nominal system voltage at the 12.5kV bus.
🧮 Baseline Unassisted Motor Start
Isc: 1.2kA
[25 empty] | X/R: 7 | [8 empty] | Parameter | [9 empty] | Unassisted |  |  |  | MotorVAR Assisted
[23 empty] | 34.5kV Bus | [19 empty] | Motor Starting Current (% of FLA): | 301.5% |  |  |  | 442.6%
[43 empty] | Motor Terminal Voltage (Percent of Rated): | 60.3% |  |  |  | 88.53% |  | ¦ ✓ 116% Higher Starting Torque ¦ ✓ 68% Lower System Inrush Current Reduction
[43 empty] | Percent of Rated Started Torque: | 36.36% |  |  |  | 78.37%
[43 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | 68.07% |  |  |  | 94.29%
🧮 MotorVAR-Assisted Motor Start - Voltage Sag Mitigation | [42 empty] | Voltage at Secondary 12.47 kV Bus: | 63.83% |  |  |  | 93.71%
[22 empty] | 12.47kV Bus | [20 empty] | Inrush current seen by system (% of FLA): | 301.5% |  |  |  | 95.99%
🧮 Simplified High-Performance Motor Starting with MotorVAR | [25 empty] | 9,923HP, 13.2kV
FLA: 351.9A
LRA: 500%
Legend:
Red: Across the line start, no assistance
Light Blue: MotorVAR assisted start
[25 empty] | Voltage change per stage at the 12.47 kV Bus: |  |  |  | ±7.12%
13.2KV, 36 MVAR
4 Stage MotorVAR
| Info@VarStec.com | [16 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [9 empty] | 4 ¦ P a g e
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION | [18 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION
Disclaimer and Use Limitation
This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
Appendix
MotorVAR Calculation Method Summary
| Info@VarStec.com | [16 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [9 empty] | 6 ¦ P a g e
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION | [18 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL SIMPLE SYSTEM CONFIGURATION
| Info@VarStec.com | [16 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [9 empty] | 8 ¦ P a g e
This spreadsheet provides preliminary sizing of VarStec’s MotorVAR solution for large medium-voltage motor starting. It models a simplified utility-to-motor system to determine the reactive power required to meet voltage-performance targets. Using utility, transformer, and motor inputs, the tool enables rapid iteration of MotorVAR sizing to limit PCC voltage drop (typically near 4%) while maintaining motor terminal voltage (typically near 90%) during across-the-line starting.
Without MotorVAR assistance, the motor draws 1061 amps (301.5% of FLA) during starting. This results in a voltage drop, with the motor terminal voltage dropping to 7.96 kV, or 60.3% of rated voltage. Correspondingly, available starting torque drops to 36.4% of rated torque, increasing the risk of stalled or prolonged motor acceleration. From a system perspective, the voltage at the 34.5 kV PCC drops to 23.48 kV, or 68.1% of rated voltage and the 12.47 kV Secondary bus drops to 7.96 kV or 63.8% of nominal voltage, or voltage drops of 31.9% and 36.2% respectively. Typical performance objectives call for a voltage of no lower than 90% of nominal at the secondary bus and 96% voltage at the primary. When these objectives are not met, alternative starting methods are typically evaluated.
With the MotorVAR system engaged, motor starting performance improves substantially. Starting current at the motor terminals is increased to 1558 amps while the current drawn through the 12.47kV system is reduced to 338 amps (96% of FLA), while motor terminal voltage is maintained at near 11.7 kV, or 88.5% of rated voltage. This enables the motor to develop approximately 78.4% of rated torque at starting, providing stronger acceleration and more stable operation. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5 kV bus remain at approximately 94.3% and 93.7% of nominal, respectively. The starting current seen by the 34.5 kV and 12.5 kV system are reduced to approximately 96 %FLA respective of the voltage levels, greatly mitigating upstream system disturbances. As the system pulls into synchronism, the 4 stage MotorVAR system limits the voltage fluctuations to approximately ±7.12%% of the nominal system voltage at the 12.5kV bus.
MotorVAR delivers fast, localized reactive power exactly where it’s needed—at the motor bus—transforming the way large medium-voltage motors are started. By actively supporting voltage during acceleration, MotorVAR mitigates voltage sags, improves power quality, and preserves starting torque, enabling the use of simple across-the-line starters without compromising system performance or plant voltage stability.
The MotorVAR system seamlessly coordinates a conventional motor starter with a smart, high-speed switched capacitor bank that is transient-free during both energization and de-energization. This approach eliminates the complexity, footprint, and operational burden typically associated with ASD/VFD solutions, synchronous bypass switchgear, E-house requirements, and the extended startup, commissioning, and lifecycle costs that accompany those systems.
A single MotorVAR installation can support multiple large motors on the same electrical system, often eliminating the need for dedicated starting equipment on each motor. Shared or cross-tie starting configurations can further enhance project economics. The result is a robust, practical motor-starting solution that minimizes system disturbance while dramatically reducing project complexity, cost, and risk.
Based on the data provided, this analysis evaluates the starting performance of a 9,923 HP, 13.2 kV motor connected to a utility system with a 34.5 kV point of common coupling (PCC). The utility short-circuit level at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, supplying the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 351.9 amps, a locked-rotor current (LRA) of 500% FLA, and a rated efficiency of 97.4% and power factor of 90%. To support motor starting, a MotorVAR system rated at 36 MVAR at 13.2kV, configured in 4 stages, is applied at the motor bus.
This spreadsheet implements a steady-state impedance model to estimate motor starting current, voltage sag, and available starting torque for a simplified medium-voltage motor starting system. All calculations are performed per phase using complex impedances.
The modeled system consists of a utility source at the point of common coupling (PCC), source impedance , transformer impedance , a secondary bus that also serves as the motor bus, and an induction motor represented by its locked-rotor impedance . A MotorVAR capacitor bank is modeled as a shunt capacitive reactance connected at the secondary bus. No additional line or cable impedance between the bus and motor is assumed. The motor rated voltage may differ from the secondary bus voltage.
Complex impedances are expressed as: . Line-to-line and phase voltages are related by: . The total upstream impedance is defined as: . Motor starting torque is approximated using the square-law voltage relationship: . Baseline Case (No MotorVAR) The motor is connected directly to the secondary bus through the upstream impedance. The equivalent load impedance is: . System and motor current: . Secondary bus and motor terminal voltage: . This case establishes baseline inrush current, voltage sag, and starting torque.
This spreadsheet implements a steady-state impedance model to estimate motor starting current, voltage sag, and available starting torque for a simplified medium-voltage motor starting system. All calculations are performed per phase using complex impedances.
The modeled system consists of a utility source at the point of common coupling (PCC), source impedance 𝑍_𝑆, transformer impedance 𝑍_𝑇, a secondary bus that also serves as the motor bus, and an induction motor represented by its locked-rotor impedance 𝑍_𝑀. A MotorVAR capacitor bank is modeled as a shunt capacitive reactance connected at the secondary bus. No additional line or cable impedance between the bus and motor is assumed. The motor rated voltage may differ from the secondary bus voltage.
Complex impedances are expressed as: 𝑍=𝑅+𝑗𝑋. Line-to-line and phase voltages are related by: 𝑉_𝑝ℎ=𝑉_𝐿𝐿/√3. The total upstream impedance is defined as: 𝑍_𝑢𝑝=𝑍_𝑆+𝑍_𝑇. Motor starting torque is approximated using the square-law voltage relationship: 𝑇_(𝑠𝑡𝑎𝑟𝑡,%)≈100%((∣𝑉_(𝑀,𝐿𝐿)∣)/𝑉_(𝑀,𝑟𝑎𝑡𝑒𝑑,𝐿𝐿) )^2. Baseline Case (No MotorVAR) The motor is connected directly to the secondary bus through the upstream impedance. The equivalent load impedance is: 𝑍_𝑒𝑞=𝑍_𝑀. System and motor current: 𝐼_𝑃𝐶𝐶=𝐼_𝑀=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑢𝑝+𝑍_𝑀 ). Secondary bus and motor terminal voltage: 𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑀,𝑝ℎ)=𝐼_𝑀 𝑍_𝑀. This case establishes baseline inrush current, voltage sag, and starting torque.
MotorVAR Case The MotorVAR capacitor bank is connected in parallel with the motor at the secondary bus. The capacitor impedance is: . The equivalent bus impedance is: . System current and bus voltage: . . Branch currents: . Motor terminal voltage equals the bus voltage. System inrush current, motor inrush current, voltage sag, and starting torque are evaluated.
MotorVAR Case The MotorVAR capacitor bank is connected in parallel with the motor at the secondary bus. The capacitor impedance is: 𝑍_𝐶=−𝑗 (𝑉_(𝑆,𝐿𝐿)^2)/𝑄_𝑀𝑉 . The equivalent bus impedance is: 𝑍_𝑒𝑞=𝑍_𝑀∥𝑍_𝐶. System current and bus voltage: 𝐼_𝑃𝐶𝐶=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑢𝑝+𝑍_𝑒𝑞 ). 𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ) 𝑍_𝑒𝑞/(𝑍_𝑢𝑝+𝑍_𝑒𝑞 ). Branch currents: 𝐼_𝑀=𝑉_(𝑆,𝑝ℎ)/𝑍_𝑀 ,𝐼_𝐶=𝑉_(𝑆,𝑝ℎ)/𝑍_𝐶 . Motor terminal voltage equals the bus voltage. System inrush current, motor inrush current, voltage sag, and starting torque are evaluated.
Step-Down Transformer
Source
M
Source
Motor
One-line diagram showing analysis results for two system configurations: the first, shown in red text, represents operation with no assistance from the MotorVAR. A standard accross the line motor start. The second, shown in light blue, represents the performance of the MotorVAR system.
Step-Down Transformer
Controls
Controls
301.5%
Current During Start (%FLA)
96.0%
1395.59
Current Assist from MotorVAR (amps)
0.0
36.4%
% Torque During Start
(amps)
Starting Current
(%FLA)
78.4%
1061
1558
301.5%
442.6%
68.1%
Voltage During Start
94.3%
63.8%
Voltage During Start
93.7%

## MotorVAR + RVSS
VarStec Power Solutions, LLC
PO Box 942
[21 empty] | Saratoga Springs, NY 12866 | MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION
[21 empty] | +1.518.369.7589 | [8 empty] | Unassisted Motor Start Results | [18 empty] | Assisted Motor Start Results / No RVSS
MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION | [38 empty] | Starting Current: | 180.525977517604-1015.17329643023i | [13 empty] | Starting Current as seen by system: | 229.588609086686-491.432104472521i | [9 empty] | 186.5628553293+152.394681109349i
[22 empty] | 📜 Motor Starting Performance Summary | [16 empty] | Starting Current: | 1031.0996 |  |  | < | -79.9166 | amps | [8 empty] | Starting Current as seen by system: | 542.4172 | < | -64.9588 | amps | [6 empty] | 240.8938 | < | 39.2438 | amps
📜 Project Details | [19 empty] | April 13, 2026 |  |  |  |  | Unassisted Start | MotorVAR Assisted1 |  | MotorVAR + RVSS Assisted2 | [10 empty] | Percent of Motor FLA: | 293% | [13 empty] | Starting Current as seen by system (% of FLA): | 154.1% | [9 empty] | 68.46%
|  |  |  | Project: | Name | [9 empty] | VarStec Ref: | VarStec Reference | [5 empty] | Parameter | [16 empty] | Percent of Rated Torque: | 34.34% | [13 empty] | Motor Current: | 174.446166361749-1300.68468468626i | [9 empty] | 117.893567262158-871.816793214711i
|  |  |  | Customer: | Name | [9 empty] | Revision #: | Rev 1 | [7 empty] | Starting Current (Magnitude and Angle): | 1031 amps, -79.9° | 1312 amps, -82.4° |  | 880 amps-82.3° | [10 empty] | Voltage at motor terminals: | 8084.45353886129-205.145468172041i | [13 empty] | Motor Current: | 1312.3308 | < | -82.3611 |  | amps | [5 empty] | 879.7519 | < | -82.2988 |  | amps |  |  | 880 amps
[24 empty] | Starting Current (% of FLA): | 293% | 372.9% |  | 250% | [10 empty] | Voltage at motor terminals: | 8087.0559 |  |  | < | -1.4536 | Volts | [8 empty] | Percent of Motor FLA: | 372.9% | [9 empty] | 250% | [6 empty] | ILIM: 250%
🧮 Purpose of Spreadsheet Tool | [23 empty] | Motor Terminal Voltage at Start: | 8.09 kV | 10.29 kV |  | 6.9 kV | [10 empty] | Percent of motor voltage rating: | 58.6% | [13 empty] | Percent of Full Torque: | 55.63% | [9 empty] | 25%
[24 empty] | Motor Terminal Voltage (% of Rating): | 58.6% | 74.59% |  | 50% | [10 empty] | Percent Voltage at Motor Bus: | 64.85% | [13 empty] | Voltage at motor terminals: | 10268.9784373805-699.727834265653i | [9 empty] | 3979.51368232418-266.81049594665i
[24 empty] | Percent of Rated Starting Torque: | 34.34% | 55.63% |  | 25% | [10 empty] | Percent voltage Sag at Motor Bus: | 35.15% | [13 empty] | Voltage at motor terminals: | 10292.7905 | < | -3.8981 | Volts | [6 empty] | 6900.0149 | < | -3.8357 | Volts
[39 empty] | Step-Down Transformer Ratio: | 2.7666 | [13 empty] | Percent of motor voltage rating: | 74.59% | [9 empty] | 50%
[39 empty] | Voltage at Primary: | 23791.382103025-365.209052517109i | [13 empty] | Percent Voltage at Motor Bus: | 82.54% | [9 empty] | 55.33%
[22 empty] | 📜 System Impact Summary | [16 empty] | Voltage at Primary: | 23794.185 |  |  | < | -0.87945 | Volts | [8 empty] | Percent voltage Sag at Motor Bus: | 17.46% | [9 empty] | 44.67%
[25 empty] | Unassisted Start | MotorVAR Assisted1 |  | MotorVAR + RVSS Assisted2 | [10 empty] | Percent of Primary Voltage Rating: | 68.97% | [13 empty] | Step-Down Transformer Ratio: | 2.7666 | [9 empty] | 2.7666
🧮 System Data | [10 empty] | System Configuration MotorVAR + RVSS | [10 empty] | Parameter | [16 empty] | Percent voltage sag at primary bus: | 31.03% | [13 empty] | Voltage at Primary: | 29107.1230479586-1639.61932796281i | [9 empty] | 7478.35311352982-447.773781527486i
Utility Source (PCC) | [23 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | 23.79 kV | 29.15 kV |  | 35.86 kV | [25 empty] | Voltage at Primary: | 29153.2668 | < | -3.2241 | Volts | [6 empty] | 35857.6499 | < | -3.4266 | Volts
[7 empty] | (Source Voltage): | 34.5 |  | kVLL | [13 empty] | Percent of Nominal: | 68.97% | 84.5% |  | 103.9% | [25 empty] | Percent of Primary Voltage Rating: | 84.5% | [9 empty] | 103.9%
[7 empty] | Short Circuit Current at Primary Vp: | 1.2 |  | kA3-phase | [13 empty] | Voltage Drop: | 31.03% | 15.5% |  | -3.935% |  |  | Utility Impedance at Motor Bus Voltage | [22 empty] | Percent voltage sag at primary bus: | 15.5% | [9 empty] | -3.935%
[7 empty] | X/R Ratio: | 7 | [22 empty] | R | 0.30704 |  |  |  |  | ohms |  |  | 2.1711 |  |  | < | 81.8699 | ohms
Step-Down Transformer | [23 empty] | Voltage at Secondary 12.47 kV Bus: | 8.09 kV | 10.3 kV |  | 13.03 kV |  |  | X | 2.1493 |  |  |  |  | ohms | [23 empty] | Calculation of K / RVSS performance
[7 empty] | Base MVA Rating: | 40 |  | MVA | [13 empty] | Percent of Nominal: | 64.85% | 82.54% |  | 104.5% |  |  | 0.307044597667228+2.1493121836706i | [10 empty] | ohms | [18 empty] | ILIM: |  | 116.943849455796-871.942772534103i |  |  | amps
[7 empty] | Secondary Voltage VS: | 12.47 |  | kVLL | [13 empty] | Voltage Drop: | 35.15% | 17.46% |  | -4.458% |  |  | Step-Down Transformer Impedance at Motor Bus Voltage | [29 empty] | Zm: |  | 0.906721069930863+4.44200792072207i
[7 empty] | Leakage Impeadance of Transformer: | 7.5 |  | % |  |  |  | 34.5kV Bus |  |  |  |  | Isc: 1.2kA X/R=7 | [11 empty] | R | 0.010171 |  |  |  |  | ohms |  |  | 0.29156 |  |  | < | 88.001 | ohms | [15 empty] | Zsys: |  | 0.317215164673209+2.44069892839196i
[7 empty] | X/R Ratio: | 28.65 | [15 empty] | Source Starting Current (34.5 kV System): | 373 amps | 196 amps |  | 87 amps |  |  | X | 0.29139 |  |  |  |  | ohms | [23 empty] | Zc: |  | -7.33494811320755i
Motor | [16 empty] | 40 MVA | [6 empty] | Source Starting Current (12.47 kV System): | 1031 amps | 542 amps |  | 241 amps |  |  | 0.0101705670059812+0.291386744721362i | [10 empty] | ohms | [18 empty] | Vs: |  | 7199.76905311778
[7 empty] | Voltage Rating: | 13.8 |  | kVLL | [6 empty] | 7.5% X/R=28.65 | [13 empty] | Locked Rotor Motor Impedance at Motor Voltage | [29 empty] | K: |  | 0.52972 | [7 empty] | Phase-phase
[7 empty] | Horse Power Rating: | 10000 |  | HP |  |  | 12.47kV Bus | [10 empty] | Percent of Motor FLA seen by system: | 293% | 154.1% |  | 68.46% |  |  | R | 0.90672 |  |  |  |  | ohms |  |  | 4.5336 |  |  | < | 78.463 | ohms | [5 empty] | Current of MotorVAR | [8 empty] | Vbus=Vsec: |  |  | 7512.53802111882-503.685664943392i | [7 empty] | 13025.8692 | < | -3.8357 | Volts
[7 empty] | Full Load Current Rating (FLA): | 351.9 |  | amps | [11 empty] | Voltage change per stage at the 12.47 kV Bus: |  |  |  |  | ±5.59% |  |  |  | X | 4.442 |  |  |  |  | ohms | [14 empty] | 0 | amps | [7 empty] | Im: |  | 117.893567262158-871.816793214711i | [7 empty] | 879.7519 | < | -82.2988 | amps
[7 empty] | Full Load Power Factor: | 90 |  | % | [20 empty] | 0.906721069930863+4.44200792072207i | [10 empty] | ohms | [9 empty] | 811.1291 | amps | [7 empty] | Vm: |  | 3979.51368232418-266.81049594665i | [7 empty] | 6900.0149 | < | -3.8357 | Volts
[7 empty] | Full Load Efficiency: | 97.4 |  | % | [9 empty] | BYPASS |  | 1: MotorVAR Performance with RVSS out of service (bypassed). | [8 empty] | MotorVAR Impedance at MotorVAR Voltage Rating | [20 empty] | 1026.5109 | amps | [7 empty] | IC: |  | 68.6692880671424+1024.21147432406i | [7 empty] | 1026.5109 | < | 86.1643 | amps
[7 empty] | Locked Rotor Current Rating (LRA): | 500 |  | % | [6 empty] | RVSS |  |  |  |  | 2: MotorVAR Performance with RVSS in operation and set at current limit of 250% FLA. | [8 empty] | R | 0 | [5 empty] | ohms | [22 empty] | Is: |  | 186.5628553293+152.394681109349i | [7 empty] | 240.8938 | < | 39.2438 | amps
[7 empty] | Locked Rotor Power Factor (PF): | 20 |  | % | [20 empty] | X | -7.3349 | [5 empty] | ohms |  |  |  | ohms | [18 empty] | Vpri: |  | 7478.35311352982-447.773781527486i | [7 empty] | 35857.6499 | < | -3.4266 | Volts
RVSS SETTING | [21 empty] | The MotorVar without the RVSS reduces the 12.47kV system's inrush current from 1031 amps (293 %FLA) to 542 amps amps (154.1 % of FLA). The voltage during starting at the 12.47 kV bus is increased from 64.9% to 82.5%. The 34.5 kV primary voltage increased from 69% to 84.5%. With both the RVSS and MotorVAR in operation, the 34.5kV system voltage during starting changes from 84.5% to 103.9% and the 12.47kV system voltage changes from 82.5% to 104.5%. Because of RVSS operation and the current at the motor being reduced from 1312 amps (372.9% FLA) to 880 amps (250% FLA), the motor torque is reduced from 55.6% of maximum torque to 25%. The MotorVAR improves RVSS performance, but at the cost of reduction in torque. Confirm the starting torque is sufficent for the load. | [8 empty] | -7.33494811320755i | [10 empty] | ohms | [18 empty] | Vsec: |  | 7520.86145355017-503.68566494339i | [7 empty] | 13040.2365 | < | -3.8315 | Volts
[7 empty] | RVSS Current Limit (ILIM): | 250 |  | % | [20 empty] | Total Impedance at Motor Voltage (unassisted)
[7 empty] | Max. Setting With MotorVAR Assist: | 372.9272 |  | % | [7 empty] | 10,000HP, 12.47kV | [12 empty] | 1.22393623460407+6.88270684911403i | [10 empty] | ohms | [20 empty] | 116.943849455796-871.942772534103i | [6 empty] | helper cells to left, keep
[7 empty] | Max. Setting Without MotorVAR Assist: | 293.0093 |  | % | [7 empty] | LRA: 500% | [20 empty] | Total Impedance at Motor | 6.9907 |  |  | < | 79.9166 | ohms | [18 empty] | 0.67037
MotorVAR | [17 empty] | FLA: 351.9A | [12 empty] | Impedance of Motor and MotorVAR System | [30 empty] | ILIM
[7 empty] | MotorVAR Voltage Rating: | 12.47 |  | kVLL | [20 empty] | 5.30754160479021+9.59903626299897i | [11 empty] | 10.9687 |  | < | 61.0607 | ohms
[7 empty] | MotorVAR Reactive Power Rating: | 21.2 |  | MVAR | [20 empty] | Total Impedance at Motor Voltage (assisted)
[7 empty] | Number of Stages: | 3 |  |  | 3 Stage MotorVAR | [19 empty] | 5.62475676946342+12.0397351913909i
[9 empty] | ` |  | 12.47KV, 21.2 MVAR | [27 empty] | Total Impedance at Motor | 13.2888 |  |  | < | 64.9588 | ohms
| Info@VarStec.com | [21 empty] | Info@VarStec.com | [5 empty] | 2 ¦ P a g e |  |  | Short Circuit Current at secondary bus: | [10 empty] | 0.377460113665694-2.90423219798979i |  |  |  |  | kA
[16 empty] | Sheet Rev Date: 1-11-2026 | [26 empty] | 2.9287 |  | kA
[41 empty] | MVA short circuit: |  | 63.1802 |  | MVAsc
MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION | [21 empty] | MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION
🧮 System Description and Inputs | [21 empty] | 📐 Simplified High-Performance Motor Starting with the MotorVAR Solution | [14 empty] | Text Box 1
This analysis evaluates the starting performance of a 10,000 HP, 13.8 kV motor connected to a utility system with a 34.5 kV point of common coupling (PCC). The utility short-circuit level at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, supplying the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 351.9 amps, a locked-rotor current (LRA) of 500% FLA, and a rated efficiency of 97.4% and power factor of 90%. A 21.2 MVAR, 12.47kV, 3 stage MotorVAR system is applied at the main secondary bus to support motor starting and to reduce system impact. In addition to the MotorVAR, and to further reduce system impacts and to reduce the rating of the MotorVAR system, an RVSS with current limit setting of 250% is also applied to the motor.
Text Box 2
Without MotorVAR or RVSS assistance, the motor draws approximately 1031.1 amps (293% of FLA) during starting. This results in significant voltage drop, with the motor terminal voltage dropping to near 8.09 kV, or 58.6% of rated voltage. Under these conditions, available starting torque drops to approximately 34.3% of rated torque, increasing the risk of stalled or prolonged motor acceleration. From a system perspective, the voltage at the 34.5 kV PCC drops to near 23.79 kV, or 69% of rated voltage while the 12.47 kV Secondary bus drops to near 8.09 kV or 64.9% of nominal. This corresponds to voltage drops of approximately 31% at the PCC and 35.1% at the secondary bus. Typical performance objectives require motor bus voltage no lower than 90% of nominal and primary voltage near 96%. When these objectives are not met, alternate starting methods are usually considered.
Text Box 3
With the MotorVAR system engaged and the RVSS out of service or bypassed, the motor starting performance improves significantly. Motor starting current increases to approximately 1312.3 amps (372.9% of FLA), while motor terminal voltage is maintained near 10.3 kV, or 74.6% of rated voltage. This allows the motor to develop approximately 55.6% of rated torque during starting, resulting in stronger acceleration and improved starting stability. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5kV secondary bus are maintained at approximately 84.5% and 82.5% of nominal, respectively. The starting current reflected into the 34.5kV and 12.5kV systems is reduced to approximately 68.5 %FLA, substantially mitigating upstream system disturbances. As the motor transitions into synchronism, the 3 stage MotorVAR system limits the voltage fluctuations to approximately ±5.59% of the nominal voltage at the 12.5kV bus.
Text Box 4:
🧮 Baseline Case: No MotorVAR or RVSS System | [36 empty] | When adding a coordinated RVSS, the combined MotorVAR + RVSS system provides additional improvement in overall system performance compared to a MotorVAR-only solution. During motor starting, the 34.5 kV bus voltage improves from approxmately 84.5% to 103.9% of nominal, while the 12.47kV bus voltage improves from approximately 82.5% to 104.5%. This improvement is driven by the RVSS current-limiting function, set to 250% of motor FLA. While current limiting improves voltage performance, it also reduces the current delivered to the motor and, consequently, the available starting torque. In this case, motor starting torque is reduced from 55.6% with MotorVAR only to approximately 25% with the combined MotorVAR + RVSS system. It is therefore critical to verify that the available starting torque remains sufficient to accelerate the driven load under all expected starting conditions.
[36 empty] | Parameter | [8 empty] | Unassisted |  |  | MotorVAR Assisted |  | MotorVAR + RVSS Assisted
[36 empty] | Motor Starting Current (% of FLA): | [8 empty] | 293% |  |  | 372.9% |  | 250%
[36 empty] | Motor Terminal Voltage (Percent of Rated): | [8 empty] | 58.6% |  |  | 74.59% |  | 50%
[36 empty] | Percent of Rated Started Torque: | [8 empty] | 34.34% |  |  | 55.63% |  | 25%
[36 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | [8 empty] | 68.97% |  |  | 84.5% |  | 103.9%
[36 empty] | Voltage at Secondary 12.47 kV Bus: | [8 empty] | 64.85% |  |  | 82.54% |  | 104.5%
[36 empty] | Inrush current seen by system (% of FLA): | [8 empty] | 293% |  |  | 154.1% |  | 68.46%
🧮 MotorVAR Only (RVSS Bypassed) | [36 empty] | ¦ ✓ 62% Higher Starting Torque ¦ ✓ 47% Lower System Inrush Current Reduction
🧮 Combined MotorVAR + RVSS
| Info@VarStec.com | [19 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [5 empty] | 4 ¦ P a g e
MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION | [21 empty] | MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION
🧮 One-Line Representation of Results | [21 empty] | Appendix
RVSS Motor Starting – Calculation Method Summary
Isc: 1.2kA
X/R: 7
34.5kV Bus
|  |  | Step Down |  |  |  |  | 40 MVA
|  |  | Transformer |  |  |  |  | 7.5% X/R=28.65
12.47kV Bus
10,000HP, 12.47kV
LRA: 500%
[10 empty] | FLA: 351.9A | [11 empty] | Equations
[12 empty] | Voltage change per stage at the 12.47 kV Bus: | [7 empty] | ±5.59%
Legend:
|  | MotorVAR System | [10 empty] | Red: Across the line start, no assistance
|  | 12.47KV, 21.2 MVAR | [10 empty] | Light Blue: MotorVAR assisted (reactor bypassed)
|  | 3 Stage MotorVAR | [10 empty] | Dark Blue: MotorVAR + RVSS assisted
| Info@VarStec.com | [19 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [5 empty] | 6 ¦ P a g e
MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION | [21 empty] | MotorVAR™ SIZING TOOL - MOTOR START CAPACITOR BANK MotorVAR + RVSS CONFIGURATION
Appendix Continued
Disclaimer and Use Limitation
This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
| Info@VarStec.com | [19 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [5 empty] | 8 ¦ P a g e
[33 empty] | CAPACITOR KVAR | 1320 | kvar
[33 empty] | CAPACITOR FREQUENCY | 50 | Hertz
[33 empty] | CAPACITOR VOLTAGE (kV) | 16 | kV
[33 empty] | CAPACITANCE (µf) | 16.41 | (µf)
[33 empty] | Xc (Ohms) | 193.9394 | Ohms
[33 empty] | RATED CURRENT | 82.5 | AMPS
When adding a coordinated RVSS, the combined MotorVAR + RVSS system provides additional improvement in overall system performance compared to a MotorVAR-only solution. During motor starting, the 34.5 kV bus voltage improves from approxmately 84.5% to 103.9% of nominal, while the 12.47kV bus voltage improves from approximately 82.5% to 104.5%. This improvement is driven by the RVSS current-limiting function, set to 250% of motor FLA. While current limiting improves voltage performance, it also reduces the current delivered to the motor and, consequently, the available starting torque. In this case, motor starting torque is reduced from 55.6% with MotorVAR only to approximately 25% with the combined MotorVAR + RVSS system. It is therefore critical to verify that the available starting torque remains sufficient to accelerate the driven load under all expected starting conditions.
ILIM: 250%
This spreadsheet provides preliminary sizing and performance evaluation of VarStec’s MotorVAR + RVSS solution for large medium-voltage motor starting. It models a simplified utility-to-motor system to evaluate the interaction between MotorVAR reactive support and RVSS current-limit settings. By iterating both MotorVAR MVAR rating and motor current limit, the tool optimizes motor terminal voltage and system voltages while maintaining sufficient current for required starting torque. This analysis extends the MotorVAR-only model by explicitly accounting for RVSS voltage reduction during starting.
Without MotorVAR or RVSS assistance, the motor draws approximately 1031.1 amps (293% of FLA) during starting. This results in significant voltage drop, with the motor terminal voltage dropping to near 8.09 kV, or 58.6% of rated voltage. Under these conditions, available starting torque drops to approximately 34.3% of rated torque, increasing the risk of stalled or prolonged motor acceleration. From a system perspective, the voltage at the 34.5 kV PCC drops to near 23.79 kV, or 69% of rated voltage while the 12.47 kV Secondary bus drops to near 8.09 kV or 64.9% of nominal. This corresponds to voltage drops of approximately 31% at the PCC and 35.1% at the secondary bus. Typical performance objectives require motor bus voltage no lower than 90% of nominal and primary voltage near 96%. When these objectives are not met, alternate starting methods are usually considered.
With the MotorVAR system engaged and the RVSS out of service or bypassed, the motor starting performance improves significantly. Motor starting current increases to approximately 1312.3 amps (372.9% of FLA), while motor terminal voltage is maintained near 10.3 kV, or 74.6% of rated voltage. This allows the motor to develop approximately 55.6% of rated torque during starting, resulting in stronger acceleration and improved starting stability. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5kV secondary bus are maintained at approximately 84.5% and 82.5% of nominal, respectively. The starting current reflected into the 34.5kV and 12.5kV systems is reduced to approximately 68.5 %FLA, substantially mitigating upstream system disturbances. As the motor transitions into synchronism, the 3 stage MotorVAR system limits the voltage fluctuations to approximately ±5.59% of the nominal voltage at the 12.5kV bus.
MotorVAR delivers fast, localized reactive power exactly where it is needed—at the motor bus—fundamentally improving the way large medium-voltage motors are started. It can be applied independently or coordinated with other starting methods, such as RVSS or reactor-start systems, to extend their effective range and further improve performance. By actively supporting voltage during acceleration, MotorVAR mitigates voltage sag, improves power quality, and preserves starting torque, enabling the use of simple across-the-line starting without compromising system performance or plant reliability.
The MotorVAR system seamlessly coordinates with a wide range of motor-starting solutions. It is a high-speed, switched capacitor bank designed to be transient-free during both energization and de-energization. This approach eliminates the complexity, footprint, and operational burden typically associated with ASD/VFD solutions, synchronous bypass switchgear, E-house requirements, and the extended startup, commissioning, and lifecycle costs that accompany those systems.
A single MotorVAR installation can support multiple large motors on the same electrical system, often eliminating the need for dedicated starting equipment at each motor. Shared or cross-tie starting configurations can further improve project economics. The result is a robust, practical motor-starting solution that minimizes system disturbance while significantly reducing project complexity, cost, and risk.
This analysis evaluates the starting performance of a 10,000 HP, 13.8 kV motor connected to a utility system with a 34.5 kV point of common coupling (PCC). The utility short-circuit level at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, supplying the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 351.9 amps, a locked-rotor current (LRA) of 500% FLA, and a rated efficiency of 97.4% and power factor of 90%. A 21.2 MVAR, 12.47kV, 3 stage MotorVAR system is applied at the main secondary bus to support motor starting and to reduce system impact. In addition to the MotorVAR, and to further reduce system impacts and to reduce the rating of the MotorVAR system, an RVSS with current limit setting of 250% is also applied to the motor.
This spreadsheet evaluates the use of a reduced-voltage soft starter (RVSS) to limit motor starting current while maintaining acceptable system voltage. The system is modeled with a finite utility source, upstream impedance, and a shunt capacitor connected at the motor bus to provide reactive voltage support.
The analysis begins by calculating the across-the-line (DOL) motor starting condition with the capacitor in service. This establishes the natural system limits, including the bus voltage and motor starting current during DOL operation. The DOL motor current defines the maximum allowable RVSS current setting.
The user then specifies a desired motor current limit, constrained not to exceed the DOL motor current. This value represents the current flowing into the motor through the RVSS, not the total system or utility current.
The RVSS is modeled as a controlled voltage device that reduces the motor terminal voltage by a factor k (0 ≤ k ≤ 1). The RVSS does not introduce any phase shift; all voltage and current angles are determined by system, motor, and capacitor impedances. The spreadsheet automatically determines the value of k required to achieve the selected motor current limit while accounting for the reactive support provided by the capacitor.
Using this value of k, the spreadsheet recalculates:
  ● Motor terminal voltage
  ● Motor current
  ● Capacitor current
  ● System (source) current
  ● Bus voltage during starting
Internal consistency checks ensure that:
  ● The calculated motor current matches the user-specified current limit
  ● When the current limit is set equal to the DOL motor current, the solution correctly returns to the DOL condition (k ≈ 1)
This tool is intended for preliminary sizing and screening of RVSS applications with capacitor support. Final designs should be confirmed using detailed motor-starting and transient studies.
103.9%
84.5%
69.0%
104.5%
82.5%
64.9%
Voltage During Start
Voltage During Start
293.0%
68.5%
154.1%
Current During Start (%FLA)
Source
Motor
% Torque During Start
Starting Current
Current Assist from MotorVAR (amps)
0.00
1027
811
25.0%
55.6%
1031
1312
880
880 amps
880 amps
34.3%
Voltage at Motor Terminals
8087
10293
6900
(Volts)
% Voltage
58.6%
74.6%
50.0%
(amps)
(% FLA)
293.0%
372.9%
250.0%
One-line diagram showing analysis results for three system configurations: the first, shown in red text, represents operation with no assistance from either the MotorVAR or the RVSS; the second, shown in light blue, represents the MotorVAR-only case with the RVSS bypassed; and the third, shown in dark blue, represents operation with both the MotorVAR + RVSS in service.
Source
M
Step-Down Transformer
Controls
Controls
ILIM: 250%

## DOL-MotorVAR-Capative XFMR
motor
VarStec Power Solutions, LLC
PO Box 942
[16 empty] | Saratoga Springs, NY 12866 | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION
[16 empty] | 518.369.7589 | [13 empty] | Unassisted Motor Start Results | [17 empty] | Assisted Motor Start Results
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION | [32 empty] | Starting Current: | 397.450193085934-2511.48530032052i | [18 empty] | Starting Current as seen by system: | 714.61730181328-665.430511522368i | [5 empty] | x
[17 empty] | 📜 Motor Starting Performance Summary | [15 empty] | Starting Current: | 2542.7397 | < | -81.0073 |  | amps | [14 empty] | Starting Current as seen by system: | 976.4608 | < | -42.9588 | amps |  |  | x
📜 Project Details | [14 empty] | April 13, 2026 | [7 empty] | Unassisted Motor Start |  |  | MotorVAR-Assisted Motor Start | [6 empty] | Percent of Motor FLA: | 382.4% | [18 empty] | Starting Current as seen by system (% of FLA): | 146.8% | [5 empty] | x
[17 empty] | Motor Parameters | [15 empty] | Percent of Rated Torque: | 34.6% | [18 empty] | Motor Current: | 299.321090912507-3950.81101829781i | [5 empty] | x
|  | Project: | Name | [6 empty] | VarStec Ref: | VarStec Reference | [10 empty] | Starting Current (Magnitude and Angle): | 2543 amps, -81° |  |  | 3962 amps, -85.7° | [6 empty] | Voltage at motor terminals: | 2350.70725879146-104.455284276813i | [18 empty] | Motor Current: | 3962.1334 | < | -85.6674 |  | amps |  | x
|  | Customer: | Name | [6 empty] | Revision #: | Rev 1 | [10 empty] | Starting Current (% of FLA): | 382.4% |  |  | 595.8% | [6 empty] | Voltage at motor terminals: | 2353.0269 | < | -2.5443 |  | Volts | [14 empty] | Percent of Motor FLA: | 595.8% | [5 empty] | x
[22 empty] | Motor Terminal Voltage at Start: | 2.35 kV |  |  | 3.67 kV | [6 empty] | Percent of motor voltage rating: | 58.83% | [18 empty] | Percent of Full Torque: | 84.02% | [5 empty] | x
🧮 Purpose of Spreadsheet Tool | [21 empty] | Motor Terminal Voltage (% of Rating): | 58.83% |  |  | 91.66% | [6 empty] | Percent Voltage at Motor Bus(sec of captive xfmr): | 56.56% | [18 empty] | Voltage at motor terminals: | 3637.57329710177-459.815964709333i | [5 empty] | x
[22 empty] | Percent of Rated Starting Torque: | 34.6% |  |  | 84.02% | [6 empty] | Percent voltage Sag at Motor Bus: | 43.44% | [18 empty] | Voltage at motor terminals: | 3666.5202 | < | -7.2044 | Volts |  |  | x
[33 empty] | Captive Transformer Ratio: | 2.9976 | [18 empty] | Percent of motor voltage rating: | 91.66% | [5 empty] | x
[17 empty] | 📜 System Impact Summary | [15 empty] | Voltage at Capative XFMR Primary: | 8859.56298574603-100.059780914041i | [18 empty] | Percent Voltage at Motor Bus (captive xfmr secondary): | 88.14% | [5 empty] | x
[23 empty] | Unassisted Motor Start |  |  | MotorVAR-Assisted Motor Start | [6 empty] | Voltage at Capative XFMR Primary: | 8860.128 | < | -0.64707 |  | Volts | [14 empty] | Percent voltage Sag at Motor Bus: | 11.86% | [5 empty] | x
[17 empty] | System Parameters | [15 empty] | Percent of Primary Capative XFMR Voltage Rating: | 71.05% | [18 empty] | Capative Transformer Ratio: | 2.9976
🧮 System Data | [21 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | 25.69 kV |  |  | 31.94 kV | [6 empty] | Percent voltage sag, capactive transformer primary: | 28.95% | [18 empty] | Voltage at capative transformer primary: | 11401.8477227741-884.785692186673i
Utility Source (PCC) | [6 empty] | System Configuration | [14 empty] | Percent of Nominal: | 74.45% |  |  | 92.57% | [6 empty] | Step-Down Transformer Rating: | 2.7666 | [18 empty] | Voltage at Primary: | 11436.126 | < | -4.4373 | Volts
|  |  |  | (Source Voltage): | 34.5 | kVLL | [15 empty] | Voltage Drop: | 25.55% |  |  | 7.429% | [6 empty] | Voltage at PCC: | 25686.1679713265-132.696928206498i | [18 empty] | Percent of Primary Voltage Rating: | 91.71%
|  |  |  | Short Circuit Current at Primary Vp: | 1.2 | kA3-phase | [26 empty] | Voltage at PCC: | 25686.5107 | < | -0.29599 |  | Volts | [14 empty] | Percent voltage sag at primary bus: | 8.291%
|  |  |  | X/R Ratio: | 7 | [16 empty] | Voltage at 12.47 kV Secondary Bus: | 8.86 kV |  |  | 11.44 kV | [6 empty] | Percent voltage at PCC, percent of nominal: | 74.45% | [18 empty] | Step-Down Transformer Rating: | 2.7666
Step-Down Transformer | [21 empty] | Percent of Nominal: | 71.05% |  |  | 91.71% | [6 empty] | Percent voltage sag, PCC: | 25.55% | [18 empty] | Voltage at PCC: | 31866.0102140006-2126.20702899064i
|  |  |  | Base MVA Rating: | 40 | MVA | [15 empty] | Voltage Drop: | 28.95% |  |  | 8.291% | [26 empty] | Voltage at PCC: | 31936.8653 | < | -3.8173 | Volts
|  |  |  | Secondary Voltage VS: | 12.47 | kVLL | [7 empty] | Isc: 1.2kA | [38 empty] | Percent voltage at PCC, percent of nominal: | 92.57%
|  |  |  | Leakage Impeadance of Transformer: | 7.5 | % |  |  | 34.5kV Bus |  |  |  |  | X/R: 7 | [7 empty] | Voltage at 4.16 kV Motor Bus: | 2353.0269 |  |  | 3666.5202 | [26 empty] | Percent voltage sag, PCC: | 7.429%
|  |  |  | X/R Ratio: | 28.65 | [7 empty] | 40 MVA | [8 empty] | Percent of Nominal: | 58.83% |  |  | 88.14%
Capative Transformer | [12 empty] | 7.5% | [8 empty] | Voltage Drop: | 56.56% |  |  | 11.86% | [24 empty] | MotorVAR Current | 3311.5247
|  |  |  | Base MVA Rating: | 10 | MVA |  |  | 12.47kV Bus
|  |  |  | Secondary Voltage VS: | 4.16 | kVLL | [15 empty] | Starting Current Seen by 34.5 kV System: | 307 amps |  |  | 117.7 amps
|  |  |  | Leakage Impeadance of Transformer: | 8 | % | [6 empty] | 10 MVA | [8 empty] | Seen by 12.47 kV System: | 848 amps |  |  | 326 amps
|  |  |  | X/R Ratio: | 25 | [7 empty] | 8% | [8 empty] | Seen by 4.16 kV System: | 2543 amps |  |  | 976
Motor | [7 empty] | 4.16kV Bus | [13 empty] | Percent of Motor FLA: | 382.4% |  |  | 146.8%
|  |  |  | Voltage Rating: | 4 | kVLL
|  |  |  | Horse Power Rating: | 5000 | HP | [7 empty] | 5,000 HP Motor |  |  | Voltage change per stage at the 4.16 kV Bus: | [8 empty] | ±9.92%
|  |  |  | Full Load Current Rating (FLA): | 665 | amps | [7 empty] | FLA: 665A |  |  | Voltage change per stage at the 12.47 kV Bus: | [8 empty] | ±2.2%
|  |  |  | Full Load Power Factor: | 90 | % | [7 empty] | LRA: 650%
|  |  |  | Full Load Efficiency: | 90 | % | [10 empty] | The MotorVar reduces the 12.47kV system's inrush current from 848 amps (382.4 %FLA) to 326 amps (146.8 % of FLA). The voltage at the 12.47 kV bus is improved from 71.1% to 91.7% while at 34.5 kV, the voltage is improved from 74.5% to 92.6%. of nominal.
|  |  |  | Locked Rotor Current Rating (LRA): | 650 | %
|  |  |  | Locked Rotor Power Factor (PF): | 20 | %
MotorVAR | [16 empty] | Note:
|  |  |  | MotorVAR Voltage Rating: | 4 | kVLL | [5 empty] | 4KV, 25 MVAR |  |  |  |  | This analysis provides preliminary MotorVAR sizing intended for feasibility assessment and system impact evaluation. Final MotorVAR configuration, staging, and protection coordination should be confirmed with a detailed engineering and dynamic motor starting study.
|  |  |  | MotorVAR Reactive Power Rating: | 25 | MVAR | [5 empty] | 3 Stage MotorVAR
|  |  |  | Number of Stages: | 3
| Info@VarStec.com | [16 empty] | Info@VarStec.com | [10 empty] | 2 ¦ P a g e
Sheet Rev Date: 1-11-2026
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION | [16 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION
🧮 Summary of Input Data | [16 empty] | 🧮 One-Line Representation of Results | [7 empty] | Legend: | [5 empty] | Utility Impedance at Motor Bus Voltage
[25 empty] | Red: Across the line start, no assistance | [5 empty] | R | 0.034171 |  |  |  | ohms |  |  |  | 0.24162 |  |  | < | 81.8699 |  | ohms
[25 empty] | Light Blue: MotorVAR assisted start | [5 empty] | X | 0.2392 |  |  |  | ohms
[31 empty] | 0.0341708053740524+0.239195637618367i | [10 empty] | ohms
Step-Down Transformer Impedance at Motor Bus Voltage
[31 empty] | R | 0.0011319 |  |  |  | ohms |  |  |  | 0.032448 |  |  | < | 88.001 |  | ohms
[31 empty] | X | 0.032428 |  |  |  | ohms
[31 empty] | 0.00113187617807169+0.032428252501754i | [10 empty] | ohms
🧮 Baseline Unassisted Motor Start | [30 empty] | Capative Transformer Impedance at Motor Bus Voltage
[24 empty] | Isc: 1.2kA | [6 empty] | R | 0.0055334 |  |  |  | ohms |  |  |  | 0.13844 |  |  | < | 87.7094 |  | ohms
[22 empty] | 34.5kV Bus |  | X/R: 7 | [6 empty] | X | 0.13833 |  |  |  | ohms
[31 empty] | 0.00553336707560184+0.138334176890046i | [10 empty] | ohms
Locked Rotor Motor Impedance at Motor Voltage
[24 empty] | 40 MVA | [6 empty] | R | 0.10698 |  |  |  | ohms |  |  |  | 0.53491 |  |  | < | 78.463 |  | ohms
[24 empty] | 7.5% | [6 empty] | X | 0.5241 |  |  |  | ohms
[21 empty] | 12.47kV Bus | [9 empty] | 0.106981549025967+0.524100414012321i | [10 empty] | ohms
MotorVAR Impedance at MotorVAR Voltage Rating
[31 empty] | R | 0 |  |  |  |  | ohms
🧮 MotorVAR-Assisted Motor Start - Voltage Sag Mitigation | [23 empty] | 10 MVA | [6 empty] | X | -0.64 |  |  |  |  | ohms |  |  |  |  | ohms
[24 empty] | 8% | [6 empty] | -0.64i | [10 empty] | ohms
[20 empty] | 4.16kV Bus | [10 empty] | Total Impedance at Motor Voltage (unassisted) | [27 empty] | Text Box 1
[31 empty] | 0.147817597653693+0.934058481022488i | [10 empty] | ohms | [16 empty] | Based on the data provided, this analysis evaluates the starting performance of a 5,000 HP, 4 kV motor connected to a utility system with a 34.5 kV point of common coupling (PCC). The motor is connected to a captive transformer having a primary voltage of 12.47kV and secondary voltage rating of 4.16kV from a 34.5/12.47 step-down transformer. The utility short-circuit level at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, supplying the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 665 amps, a locked-rotor current (LRA) of 650% FLA, and a rated efficiency of 90% and power factor of 90%. To support motor starting, a MotorVAR system rated at 25 MVAR at 4kV, configured in 3 stages, is applied at the motor bus.
[39 empty] | Total Impedance at Motor | 0.94568 |  |  | < | 81.0073 |  | ohms
[31 empty] | Impedance of Motor and MotorVAR System | [27 empty] | Text Box 2
[31 empty] | 1.76139781684541+1.26822884497993i | [11 empty] | 2.1705 |  |  | < | 35.7544 |  | ohms | [9 empty] | Without MotorVAR assistance, the motor draws approximately 2543 amps (382.4% of FLA) during starting. This results in a voltage drop, with the motor terminal voltage dropping to near 2.35 kV, or 58.8% of rated voltage. Correspondingly, available starting torque drops to approximately 34.6% of rated torque, increasing the risk of stalled or prolonged motor acceleration. From a system perspective, the voltage at the 34.5 kV PCC drops to near 25.69 kV, or 74.5% of rated voltage and the 12.47 kV secondary bus drops to near 8.86 kV or 71.1% of nominal voltage, representing a voltage sags of near 25.5% and 28.9% respectively. Typical performance objectives call for a voltage of no lower than 90% of nominal at the secondary bus and 96% voltage at the primary. When these objectives are not met, alternate starting means are necessary. The starting current reflected into the utility system is approximately 307 amps at 34.5 kV, or 382.4% FLA.
Total Impedance at Motor Voltage (assisted)
[31 empty] | 1.80223386547314+1.6781869119901i | [27 empty] | Text Box 3
🧮 Simplified High-Performance Motor Starting with MotorVAR | [24 empty] | 5,000 HP Motor | [13 empty] | Total Impedance at Motor | 2.4626 |  |  | < | 42.9588 |  | ohms | [12 empty] | With the MotorVAR system engaged, motor starting performance improves substantially. Starting current at the motor terminals is increased to 3962.1 amps (146.8% of FLA), while motor terminal voltage is maintained at near 3.7 kV, or 91.7% of rated voltage. This enables the motor to develop approximately 84% of rated torque at starting, providing stronger acceleration and more stable operation. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5 kV bus remain at approximately 92.6% and 91.7% of nominal, respectively. The starting current seen by the 34.5 kV and 12.5 kV system are reduced to approximately 146.8 %FLA respective of voltage transformations, greatly mitigating upstream system disturbances. As the system pulls into synchronism, the 3 stage MotorVAR system limits the voltage fluctuations to approximately ±2.2%% of the nominal system voltage at the 12.5kV bus and ±9.92% at the 4.16 kV bus.
FLA: 665A
[25 empty] | LRA: 650% | [5 empty] | Short Circuit Current at motor bus: | [9 empty] | Short Circuit Current at at 4.16kV bus: | 0.578527678568157-5.80790984406487i | [7 empty] | kA
[41 empty] | Short Circuit Current at at 4.16kV bus: | 5.8367 |  |  | kA
[27 empty] | Voltage change per stage at the 4.16 kV Bus: | ±9.92% | [12 empty] | MVA short circuit at 4.16kV bus: | 42.0052 |  |  | MVAsc
[27 empty] | Voltage change per stage at the 12.47 kV Bus: | ±2.2%
[41 empty] | Short Circuit Current at at 12.47kV bus: | 1.13147298495462-8.70571526657035i
[41 empty] | Short Circuit Current at at 12.47kV bus: | 8.7789 |  |  | kA
[41 empty] | MVA Circuit Current at at 12.47kV bus: | 189.3889
3 Stage MotorVAR
4KV, 25 MVAR
| Info@VarStec.com | [14 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [10 empty] | 4 ¦ P a g e
[35 empty] | Parameter | [10 empty] | Unassisted | [5 empty] | MotorVAR Assisted
[45 empty] | Motor Starting Current (% of FLA): | 382.4% | [5 empty] | 595.8%
[45 empty] | Inrush current seen by system (% of FLA): | 382.4% | [5 empty] | 146.8% |  |  | ¦ ✓ 143% Higher Starting Torque ¦ ✓ -50% Lower System Inrush Current Reduction
[45 empty] | Percent of Rated Started Torque: | 34.6% | [5 empty] | 84.02%
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION | [16 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION | [27 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | 74.45% | [5 empty] | 92.57%
[45 empty] | Voltage at 12.47 kV Secondary Bus: | 71.05% | [5 empty] | 91.71%
[17 empty] | Appendix | [27 empty] | Voltage at 4.16 kV Motor Bus: | 58.83% | [5 empty] | 88.14%
[45 empty] | Motor Terminal Voltage (Percent of Rated): | 58.83% | [5 empty] | 91.66%
MotorVAR + Captive Transformer Calculation Method Summary
| Info@VarStec.com | [14 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [10 empty] | 6 ¦ P a g e
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION | [16 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL CAPTIVE TRANSFORMER CONFIGURATION
Disclaimer and Use Limitation
This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
| Info@VarStec.com | [14 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [10 empty] | 8 ¦ P a g e
This spreadsheet provides preliminary sizing of VarStec’s MotorVAR solution for large medium-voltage motor starting. It models a simplified system, utility source, transformer, and motor bus connected to the network through a captive transfomer to determine the reactive power required to meet voltage-performance targets. Inputs include utility short-circuit strength, transformer data, and motor parameters, enabling rapid iteration of the MotorVAR's reactive power rating to limit PCC voltage drop (typically to near ~4% ) while maintaining motor terminal voltage. (typically to near ~90 ).
Without MotorVAR assistance, the motor draws approximately 2543 amps (382.4% of FLA) during starting. This results in a voltage drop, with the motor terminal voltage dropping to near 2.35 kV, or 58.8% of rated voltage. Correspondingly, available starting torque drops to approximately 34.6% of rated torque, increasing the risk of stalled or prolonged motor acceleration. From a system perspective, the voltage at the 34.5 kV PCC drops to near 25.69 kV, or 74.5% of rated voltage and the 12.47 kV secondary bus drops to near 8.86 kV or 71.1% of nominal voltage, representing a voltage sags of near 25.5% and 28.9% respectively. Typical performance objectives call for a voltage of no lower than 90% of nominal at the secondary bus and 96% voltage at the primary. When these objectives are not met, alternate starting means are necessary. The starting current reflected into the utility system is approximately 307 amps at 34.5 kV, or 382.4% FLA.
With the MotorVAR system engaged, motor starting performance improves substantially. Starting current at the motor terminals is increased to 3962.1 amps (146.8% of FLA), while motor terminal voltage is maintained at near 3.7 kV, or 91.7% of rated voltage. This enables the motor to develop approximately 84% of rated torque at starting, providing stronger acceleration and more stable operation. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5 kV bus remain at approximately 92.6% and 91.7% of nominal, respectively. The starting current seen by the 34.5 kV and 12.5 kV system are reduced to approximately 146.8 %FLA respective of voltage transformations, greatly mitigating upstream system disturbances. As the system pulls into synchronism, the 3 stage MotorVAR system limits the voltage fluctuations to approximately ±2.2%% of the nominal system voltage at the 12.5kV bus and ±9.92% at the 4.16 kV bus.
MotorVAR delivers fast, localized reactive power exactly where it’s needed, at the motor bus, transforming the way large medium-voltage motors are started. By actively supporting voltage during acceleration, MotorVAR mitigates voltage sags, improves power quality, and preserves starting torque, enabling the use of simp le across-the-line starters without compromising system performance or plant voltage stability.
The MotorVAR system seamlessly coordinates a conventional motor starter with a smart, high-speed switched capacitor bank that is transient-free during both energization and de-energization. This approach eliminates the complexity, footprint, and operational burden typically associated with ASD/VFD solutions, synchronous bypass switchgear, E-house requirements, and the extended startup, commissioning, and lifecycle costs that accompany those systems.
A single MotorVAR installation can support multiple large motors on the same electrical system, often eliminating the need for dedicated starting equipment on each motor. Shared or cross-tie starting configurations can further enhance project economics. The result is a robust, practical motor-starting solution that minimizes system disturbance while dramatically reducing project complexity, cost, and risk.
Based on the data provided, this analysis evaluates the starting performance of a 5,000 HP, 4 kV motor connected to a utility system with a 34.5 kV point of common coupling (PCC). The motor is connected to a captive transformer having a primary voltage of 12.47kV and secondary voltage rating of 4.16kV from a 34.5/12.47 step-down transformer. The utility short-circuit level at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, supplying the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 665 amps, a locked-rotor current (LRA) of 650% FLA, and a rated efficiency of 90% and power factor of 90%. To support motor starting, a MotorVAR system rated at 25 MVAR at 4kV, configured in 3 stages, is applied at the motor bus.
This spreadsheet implements a steady-state impedance-based model to estimate motor starting current, voltage sag, and available starting torque for a medium-voltage motor starting through a captive transformer. All calculations are performed using complex impedances and phasor relationships and are converted to three-phase quantities where required.
The modeled system consists of a utility source at the point of common coupling (PCC), source impedance , a step-down transformer with impedance , a motor bus, a captive transformer represented by its equivalent impedance , and an induction motor represented by its locked-rotor impedance . The MotorVAR solution is integrated within the captive transformer configuration to provide local reactive power support at the motor bus. No additional line or cable impedance between elements is assumed. The motor rated voltage may differ from the transformer secondary or motor bus voltage.
Complex impedances are expressed as: . Line-to-line and phase voltages are related by: . The total upstream impedance from the PCC to the motor bus is defined as: .
Motor starting torque is approximated using the square-law voltage relationship:
Baseline Case (No MotorVAR Support) In the baseline configuration, the motor is supplied through the source, step-down transformer, and captive transformer impedances without reactive power support. The equivalent load impedance is:
System and motor current are:
Motor bus and motor terminal voltage are:
Primary voltage at the PCC is calculated by:
This case establishes baseline inrush current, PCC voltage sag, motor bus voltage, and starting torque.
MotorVAR-Assisted Start with Capacitive Transformer In the MotorVAR-assisted configuration, the captive transformer provides reactive power support to the motor bus, reducing current drawn from the upstream system and improving voltage performance during motor starting.
The captive transformer impedance is treated as part of the upstream network supplying the motor, and the effective system impedance remains:
System and motor current are:
This spreadsheet implements a steady-state impedance-based model to estimate motor starting current, voltage sag, and available starting torque for a medium-voltage motor starting through a captive transformer. All calculations are performed using complex impedances and phasor relationships and are converted to three-phase quantities where required.
The modeled system consists of a utility source at the point of common coupling (PCC), source impedance 𝑍_𝑆, a step-down transformer with impedance 𝑍_𝑇, a motor bus, a captive transformer represented by its equivalent impedance 𝑍_𝐶, and an induction motor represented by its locked-rotor impedance 𝑍_𝑀. The MotorVAR solution is integrated within the captive transformer configuration to provide local reactive power support at the motor bus. No additional line or cable impedance between elements is assumed. The motor rated voltage may differ from the transformer secondary or motor bus voltage.
Complex impedances are expressed as: 𝑍=𝑅+𝑗𝑋. Line-to-line and phase voltages are related by: 𝑉_𝑝ℎ=𝑉_𝐿𝐿/√3. The total upstream impedance from the PCC to the motor bus is defined as: 𝑍_𝑢𝑝=𝑍_𝑆+𝑍_𝑇+𝑍_𝐶.
Motor starting torque is approximated using the square-law voltage relationship:
𝑇_(𝑠𝑡𝑎𝑟𝑡,%)≈100%((∣𝑉_(𝑀,𝐿𝐿)∣)/𝑉_(𝑀,𝑟𝑎𝑡𝑒𝑑,𝐿𝐿) )^2
Baseline Case (No MotorVAR Support) In the baseline configuration, the motor is supplied through the source, step-down transformer, and captive transformer impedances without reactive power support. The equivalent load impedance is:
𝑍_𝑒𝑞=𝑍_𝑀
System and motor current are:
𝐼_𝑃𝐶𝐶=𝐼_𝑀=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑆+𝑍_𝑇+𝑍_𝐶+𝑍_𝑀 )
Motor bus and motor terminal voltage are:
𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑀,𝑝ℎ)=𝐼_𝑀 𝑍_𝑀
Primary voltage at the PCC is calculated by:
𝑉_(𝑃𝐶𝐶,𝑝ℎ)=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)−𝐼_𝑃𝐶𝐶 𝑍_𝑆
This case establishes baseline inrush current, PCC voltage sag, motor bus voltage, and starting torque.
MotorVAR-Assisted Start with Capacitive Transformer In the MotorVAR-assisted configuration, the captive transformer provides reactive power support to the motor bus, reducing current drawn from the upstream system and improving voltage performance during motor starting.
The captive transformer impedance 𝑍_𝐶is treated as part of the upstream network supplying the motor, and the effective system impedance remains:
𝑍_𝑢𝑝=𝑍_𝑆+𝑍_𝑇+𝑍_𝐶
System and motor current are:
𝐼_𝑃𝐶𝐶=𝐼_𝑀=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑢𝑝+𝑍_𝑀 )
Motor bus and motor terminal voltage are:
Primary voltage at the PCC is:
MotorVAR reactive support can be iteratively adjusted within the captive transformer design to achieve performance targets, typically limiting PCC voltage drop to approximately 4% while maintaining motor terminal voltage near 90% of rated value during starting. Starting torque is evaluated from the resulting motor terminal voltage using the square-law relationship.
Motor bus and motor terminal voltage are:
𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑀,𝑝ℎ)=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ) 𝑍_𝑀/(𝑍_𝑢𝑝+𝑍_𝑀 )
Primary voltage at the PCC is:
𝑉_(𝑃𝐶𝐶,𝑝ℎ)=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)−𝐼_𝑃𝐶𝐶 𝑍_𝑆
MotorVAR reactive support can be iteratively adjusted within the captive transformer design to achieve performance targets, typically limiting PCC voltage drop to approximately 4% while maintaining motor terminal voltage near 90% of rated value during starting. Starting torque is evaluated from the resulting motor terminal voltage using the square-law relationship.
Controls
Controls
Step-Down Transformer
Capative Transformer
Step-Down Transformer
Capative Transformer
Source
M
Source
Motor
Current During Start (%FLA)
382.4%
146.8%
Voltage During Start
74.5%
Voltage During Start
Voltage During Start
92.6%
71.1%
91.7%
58.8%
88.1%
3312
Current Assist from MotorVAR (amps)
0.0
34.6%
% Torque During Start
(amps)
Starting Current
(%FLA)
84.0%
382.4%
595.8%
2543
3962
One-line diagram showing analysis results for two system configurations: the first, shown in red text, represents operation with no assistance from the MotorVAR. A standard accross the line motor start. The second, shown in light blue, represents the performance of the MotorVAR system.

## DOL-MotorVAR + Reactor
VarStec Power Solutions, LLC
PO Box 942
[21 empty] | Saratoga Springs, NY 12866 | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL MotorVAR + LINE REACTOR CONFIGURATION
[21 empty] | 518.369.7589 | [9 empty] | Unassisted Motor Start Results | [18 empty] | Assisted Motor Start Results With Reactor | [17 empty] | Assisted Motor Start Results Without Reactor
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL MotorVAR + LINE REACTOR CONFIGURATION | [36 empty] | Starting Current: | 190.725597987928-1083.15358328966i | [15 empty] | Starting Current as seen by system: | 172.267801931318-95.2265395005787i | [14 empty] | Starting Current as seen by system: | 253.459665663731-488.052841389053i
[22 empty] | 📜 Motor Starting Performance Summary | [14 empty] | Starting Current: | 1099.8172 |  |  | < | -80.0135 |  | amps | [9 empty] | Starting Current as seen by system: | 196.8357 |  | < | -28.933 | amps | [10 empty] | Starting Current as seen by system: | 549.9431 | < | -62.5559 | amps
📜 Project Details | [19 empty] | April 13, 2026 |  |  |  |  | Unassisted Motor Start1 | MotorVAR Assisted2 |  | MotorVAR + Reactor Assisted3 | [8 empty] | Percent of Motor FLA: | 312.5% | [15 empty] | Starting Current as seen by system (% of FLA): | 55.94% | [14 empty] | Starting Current as seen by system (% of FLA): | 156.3%
[22 empty] | Parameter | [14 empty] | Percent of Rated Torque: | 39.07% | [15 empty] | Motor Bus Voltage (secondary bus voltage): | 11973.3770793171-675.126509289004i | [14 empty] | Motor Bus Voltage (secondary bus voltage): | 10270.1470569539-802.375681431261i
|  | Project: | Name | [10 empty] | VarStec Ref: | VarStec Reference | [8 empty] | Starting Current (Magnitude and Angle): | 1100 amps, -80° | 1454 amps, -82.9° |  |  | 1213 amps, -84.8° | [7 empty] | Voltage at motor terminals: | 7791.81558335364-210.90606518205i | [15 empty] | Motor Bus Voltage (Secondary Bus Voltage): | 11992.3957 |  | < | -3.2272 | Volts | [10 empty] | Motor Bus Voltage (Secondary Bus Voltage): | 10301.443 | < | -4.4673 | Volts
|  | Customer: | Name | [10 empty] | Revision #: | Rev 1 | [8 empty] | Starting Current (% of FLA): | 312.5% | 413% |  |  | 344.7% | [7 empty] | Voltage at motor terminals: | 7794.6694 |  |  | < | -1.5505 |  | Volts | [9 empty] | Percent Voltage at Motor Bus: | 96.17% | [14 empty] | Percent Voltage at Motor Bus: | 82.61%
[24 empty] | Motor Terminal Voltage at Start: | 7.79 kV | 10.3 kV |  |  | 8.6 kV | [7 empty] | Percent of motor voltage rating: | 62.51% | [15 empty] | Percent voltage Sag at Motor Bus: | 3.83% | [14 empty] | Percent voltage Sag at Motor Bus: | 17.39%
🧮 Purpose of Spreadsheet Tool | [23 empty] | Motor Terminal Voltage (% of Rating): | 62.51% | 82.61% |  |  | 68.93% |  |  |  | Voltage at Motor Bus: |  |  |  |  | 7791.81558335364-210.90606518205i | [15 empty] | Voltage at motor terminals: | 8543.14350708119-951.606853955736i | [14 empty] | Voltage at motor terminals: | 10270.1470569539-802.375681431261i
[24 empty] | Percent of Rated Starting Torque: | 39.07% | 68.24% |  |  | 47.52% | [7 empty] | Voltage at Motor Bus: | 7794.6694 |  |  | < | -1.5505 |  | amps | Volts | [8 empty] | Voltage at motor terminals: | 8595.9791 |  | < | -6.3559 | Volts | [10 empty] | Voltage at motor terminals: | 10301.443 | < | -4.4673 | Volts
[37 empty] | Percent Voltage at Motor Bus: | 62.51% | [15 empty] | Percent of motor voltage rating: | 68.93% | [14 empty] | Percent of motor voltage rating: | 82.61%
[37 empty] | Percent voltage Sag at Motor Bus: | 37.49%
[22 empty] | 📜 System Impact Summary | [14 empty] | Step-Down Transformer Ratio: | 2.7666
[25 empty] | Unassisted Motor Start1 | MotorVAR Assisted2 |  | MotorVAR + Reactor Assisted3 | [8 empty] | Voltage at Primary: | 23077.064187107-370.230770930219i | [15 empty] | Step-Down Transformer Ratio: | 2.7666 | [14 empty] | Step-Down Transformer Ratio: | 2.7666
[22 empty] | Parameter | [14 empty] | Voltage at Primary: | 23080.0338 |  |  | < | -0.91913 |  | Volts |  |  |  |  | x |  |  |  |  | Voltage at Primary: | 33267.2177666557-1632.212400765i | [14 empty] | Voltage at Primary: | 29106.8052976283-1890.15243882874i
[24 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | 23.08 kV | 29.17 kV |  | 33.31 kV | [8 empty] | Percent of Primary Voltage Rating: | 66.9% | [10 empty] | x |  |  |  |  | Voltage at Primary: | 33307.2349 |  | < | -2.8089 | Volts | [10 empty] | Voltage at Primary: | 29168.1126 | < | -3.7155 | Volts
🧮 System Data | [9 empty] | System Configuration MotorVAR + Reactor | [13 empty] | Percent of Nominal: | 66.9% | 84.55% |  | 96.54% | [8 empty] | Percent voltage sag at primary bus: | 33.1% | [10 empty] | x |  |  |  |  | Percent of Primary Voltage Rating: | 96.54% | [14 empty] | Percent of Primary Voltage Rating: | 84.55%
Utility Source (PCC) | [23 empty] | Voltage Drop: | 33.1% | 15.45% |  | 3.457% | [20 empty] | x |  |  |  |  | Percent voltage sag at primary bus: | 3.457% | [14 empty] | Percent voltage sag at primary bus: | 15.45%
[5 empty] | (Source Voltage): | 34.5 |  | kVLL
[5 empty] | Short Circuit Current at Primary Vp: | 1.2 |  | kA3-phase | [15 empty] | Voltage at Secondary 12.47 kV Bus: | 7.79 kV | 10.3 kV |  | 11.99 kV |  |  |  | Utility Impedance at Motor Bus Voltage | [16 empty] | x |  |  |  |  | Motor Current: | 109.52756422831-1207.92543923012i | [14 empty] | Motor Current: | 178.894024576512-1442.46873045958i
[5 empty] | X/R Ratio: | 7 | [17 empty] | Percent of Nominal: | 62.51% | 82.61% |  | 96.17% |  |  |  | R | 0.30704 |  | ohms |  |  | 2.1711 |  |  | < | 81.8699 |  | ohms |  |  |  |  | x |  |  |  |  | Motor Current: | 1212.8809 |  | < | -84.8189 |  | amps | [9 empty] | Motor Current: | 1453.5196 | < | -82.9303 |  | amps
Step-Down Transformer | [23 empty] | Voltage Drop: | 37.49% | 17.39% |  | 3.83% |  |  |  | X | 2.1493 |  | ohms | [13 empty] | x |  |  |  |  | Percent of Motor FLA: | 344.7% | [14 empty] | Percent of Motor FLA: | 413%
[5 empty] | Base MVA Rating: | 40 |  | MVA | [23 empty] | 0.307044597667228+2.1493121836706i | [7 empty] | ohms | [8 empty] | x |  |  |  |  | Percent of Full Torque: | 47.52% | [14 empty] | Percent of Full Torque: | 68.24%
[5 empty] | Secondary Voltage VS: | 12.47 |  | kVLL | [8 empty] | Isc: 1.2kA | [6 empty] | Starting Current Seen by 34.5 kV System: | 398 amps | 199 amps |  | 71 amps |  |  |  | Step-Down Transformer Impedance at Motor Bus Voltage
[5 empty] | Leakage Impeadance of Transformer: | 7.5 |  | % |  |  |  |  | 34.5kV Bus |  |  |  | X/R: 7 | [6 empty] | Starting Current Seen by 12.47 kV System: | 1100 amps | 550 amps |  | 197 amps |  |  |  | R | 0.010171 |  | ohms |  |  | 0.29156 |  |  | < | 88.001 |  | ohms
[5 empty] | X/R Ratio: | 28.65 | [9 empty] | 40 MVA | [15 empty] | X | 0.29139 |  | ohms
Starting-Reactor | [15 empty] | 7.5% | [7 empty] | Percent of Motor FLA seen by system: | 312.5% | 156.3% |  | 55.94% |  |  |  | 0.0101705670059812+0.291386744721362i | [7 empty] | ohms | [7 empty] | MotorVAR current:
[5 empty] | Inductive Reactance of Reactor: | 1.64 |  | Ohms |  |  |  |  | 12.47kV Bus | [8 empty] | Voltage change per stage at the 12.47 kV Bus: |  |  |  |  | ±4.95% |  |  |  |  | Locked Rotor Motor Impedance at Motor Voltage | [15 empty] | No Assist: |  |  |  | 0 | amps
[5 empty] | X/R Ratio: | 100 | [16 empty] | 1:Performance with MotorVAR out of service and reactor bypassed (an across the line start with no assistance). | [8 empty] | R | 0.81933 |  | ohms |  |  | 4.0967 |  |  | < | 78.463 |  | ohms |  |  |  | Bypassed: |  |  |  | 957.3243 | amps
Motor | [22 empty] | 2: MotorVAR performance with reactor bypassed. | [8 empty] | X | 4.0139 |  | ohms | [12 empty] | MotorVAR + Reactor |  |  |  | 1114.4663 | amps
[5 empty] | Voltage Rating: | 12.47 |  | kVLL | [10 empty] | 1.64 ohms |  |  |  | 3: MotorVAR + Reactor Performance | [8 empty] | 0.819334184205643+4.01390136024669i | [7 empty] | ohms
[5 empty] | Horse Power Rating: | 9923 |  | HP | [10 empty] | X/R:100 | [12 empty] | Reactor Impedance
[5 empty] | Full Load Current Rating (FLA): | 351.9 |  | amps | [13 empty] | Table Summary | [9 empty] | R | 0.0164 |  |  | ohms
[5 empty] | Full Load Power Factor: | 90 |  | % | [13 empty] | With the reactor bypassed, the MotorVAR system reduces the 12.47 kV system inrush current from 1100 amps amps (312.5% FLA) to 550 amps amps (156.3% FLA). The minimum starting voltage at the 12.47 kV bus improves from 62.5% to 82.6%, while the 34.5 kV PCC voltage improves from 66.9% to 84.5%. Available starting torque increases from 39.1% to 68.2%. When a line reactor is added and coordinated with the MotorVAR system, the starting current seen by the motor is further reduced from 413% FLA to 344.7% FLA, with a corresponding reduction in available starting torque from 68.2% to 47.5%. Despite the reduced torque, voltage performance improves due to the lower current demand. The minimum starting voltage at the 34.5 kV PCC increases from 84.5% to 96.5%, while the 12.47 kV bus voltage improves from 82.6% to 96.2%. | [9 empty] | X | 1.64 |  |  | ohms |  |  |  | ohms
[5 empty] | Full Load Efficiency: | 97.4 |  | % | [9 empty] | 9,923HP, 12.47kV | [13 empty] | 0.0164+1.64i | [7 empty] | ohms
[5 empty] | Locked Rotor Current Rating (LRA): | 500 |  | % | [9 empty] | LRA: 500% | [13 empty] | MotorVAR Impedance at MotorVAR Voltage Rating
[5 empty] | Locked Rotor Power Factor (PF): | 20 |  | % | [9 empty] | FLA: 351.9A | [13 empty] | R | 0 |  |  | ohms
MotorVAR | [31 empty] | X | -6.22 |  |  | ohms |  |  |  | ohms
[5 empty] | MotorVAR Voltage Rating: | 12.47 |  | kVLL | [23 empty] | -6.220036i | [7 empty] | ohms
[5 empty] | MotorVAR Reactive Power Rating: | 25 |  | MVAR | [23 empty] | Total Impedance at Motor Voltage (source, transformer, reactor, motor)
[5 empty] | Number of Stages: | 4 |  |  |  |  | 12.47KV, 25 MVAR | [19 empty] | x | 1.15294934887885+8.09460028863865i | [7 empty] | ohms
[11 empty] | 4 Stage MotorVAR | [25 empty] | Total Impedance at Motor | 8.1763 |  |  | < | 81.8936 |  | ohms
| Info@VarStec.com | [21 empty] | Info@VarStec.com | [6 empty] | 2 ¦ P a g e
[15 empty] | Sheet Rev Date: 1-11-26 | [16 empty] | Impedance of Motor, Reactor Start, and MotorVAR System | [23 empty] | Impedance of Motor and MotorVAR System (Reactor ByPassed)
[31 empty] | xx | 31.7319530506234+15.2755042668599i | [8 empty] | 35.2173 |  |  | < | 25.7058 | ohms | [9 empty] | 5.72357490863051+9.19122977233526i | [5 empty] | 10.8277 |  |  | < | 58.0886 |  |  | ohms
[32 empty] | Total Impedance at Motor Bus Voltage (assisted, includes motor, motorVAR, Reactor, StepDown XFMR, and utility impedance) | [23 empty] | Total Impedance at Motor Bus Voltage (assisted start, includes motor, motorVAR, StepDown XFMR, and utility impedance, Reactor is bypassed)
[32 empty] | 32.0491682152966+17.7162031952519i | [23 empty] | 6.04079007330372+11.6319287007272i
[37 empty] | Total Impedance at Motor | 36.6198 |  |  | < | 28.933 |  | ohms | [15 empty] | Total Impedance at Motor | 13.107 |  | < | 62.5559 |  |  | ohms
MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL MotorVAR + LINE REACTOR CONFIGURATION | [21 empty] | MotorVAR™ - MOTOR START CAPACITOR BANK - SIZING TOOL MotorVAR + LINE REACTOR CONFIGURATION
[31 empty] | Short Circuit Current at secondary bus: | [7 empty] | 0.377460113665694-2.90423219798979i | [7 empty] | kA
🧮 System Description and Inputs | [21 empty] | 📐 Simplified High-Performance Motor Starting with the MotorVAR Solution | [16 empty] | 2.9287 |  |  |  | kA
[38 empty] | MVA short circuit: | 63.1802 |  |  |  | MVAsc
[34 empty] | Parameter | [8 empty] | Unassisted Start |  |  |  | MotorVAR Assisted |  |  |  | MotorVAR + Reactor Assisted
[34 empty] | Motor Starting Current (% of FLA): | [8 empty] | 312.5% |  |  |  | 413% |  |  |  | 344.7%
[34 empty] | Motor Terminal Voltage (Percent of Rated): | [8 empty] | 62.51% |  |  |  | 82.61% |  |  |  | 68.93%
[34 empty] | Percent of Rated Started Torque: | [8 empty] | 39.07% |  |  |  | 68.24% |  |  |  | 47.52%
🧮 Baseline Case: No MotorVAR or MotorVAR + Reactor System | [33 empty] | Voltage at Primary (PCC) 34.5 kV Bus: | [8 empty] | 66.9% |  |  |  | 84.55% |  |  |  | 96.54%
[34 empty] | Voltage at Secondary 12.47 kV Bus: | [8 empty] | 62.51% |  |  |  | 82.61% |  |  |  | 96.17%
[34 empty] | Inrush current seen by system (% of FLA): | [8 empty] | 312.5% |  |  |  | 156.3% |  |  |  | 55.94%
Text Box 1
This analysis evaluates the starting performance of a 9,923 HP, 12.47 kV motor supplied from a 34.5 kV utility system at the point of common coupling (PCC). The available utility short-circuit strength at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, feeding the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 351.9 amps, a locked-rotor current (LRA) of 500% of FLA, a rated efficiency of 97.4%, and a power factor of 90%. To enhance starting performance and mitigate system disturbances, a starting reactor rated at 1.64 ohms is coordinated with a 25 MVAR, 12.47 kV, 4-stage MotorVAR system to provide controlled, high-performance starting assistance.
Text Box 2
Without MotorVAR or reactor start assistance, the motor draws approximately 1099.8 amps (312.5% of FLA) during starting. This high inrush current results in a significant voltage drop, with motor terminal voltage dropping to approximately 7.79 kV, or 62.5% of rated voltage. As a result, available starting torque is reduced to roughly 39.1% of rated torque, increasing the likelihood of extended acceleration times or a stalled start condition. From a system perspective, voltage at the 34.5 kV PCC drops to approximately 23.08 kV, or 66.9% of nominal, while the 12.47 kV secondary bus voltage falls to 7.79 kV, or 62.5% of rated voltage. These correspond to voltage drops of 33.1% at the PCC and 37.5% at the secondary bus. Typical design objectives require no less than 96% voltage at the PCC and 90% voltage at the motor bus during starting. When these criteria are not met, alternative starting methods are usually evaluated.
🧮 MotorVAR Only (Reactor Bypassed) | [31 empty] | Text Box 3
When adding a coordinated line reactor, the combined MotorVAR + Reactor system provides additional improvement in overall system performance compared to a MotorVAR-only solution. During motor starting, the 34.5 kV bus voltage improves from 84.5% to 96.5% of nominal, while the 12.47kV bus voltage improves from 82.6% to 96.2%. This improvement is driven by the current-limiting action of the line reactor (1.64 ohms). While current limiting improves voltage performance, it also reduces the current delivered to the motor and, consequently, the available starting torque. In this case, motor starting torque is reduced from 68.2% with MotorVAR only to approximately 47.5% with the combined MotorVAR + Reactor system. It is therefore critical to verify that the available starting torque remains sufficient to accelerate the driven load under all expected starting conditions.
Text Box 4
With the MotorVAR system engaged and line reactor out of service or bypassed, the motor starting performance improves significantly. Motor starting current increases to approximately 1453.5 amps (413% of FLA), while motor terminal voltage is maintained near 10.3 kV, or 82.6% of rated voltage. This allows the motor to develop approximately 68.2% of rated torque during starting, resulting in stronger acceleration and improved starting stability. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5kV secondary bus are maintained at approximately 96.5% and 96.2% of nominal, respectively. The starting current reflected into the 34.5kV and 12.5kV systems is reduced to approximately 156.3 %FLA, substantially mitigating upstream system disturbances. As the motor transitions into synchronism, the 4 stage MotorVAR system limits the voltage fluctuations to approximately ±4.95%% of the nominal voltage at the 12.5kV bus.
🧮 Combined MotorVAR + Line Reactor
| Info@VarStec.com | [19 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [6 empty] | 4 ¦ P a g e
MotorVAR™ SIZING TOOL, MotorVar ¦ REACTOR-ASSISTED MOTOR START SYSTEM | [21 empty] | MotorVAR™ SIZING TOOL, MotorVar ¦ REACTOR-ASSISTED MOTOR START SYSTEM
🧮 One-Line Representation of Results | [21 empty] | Appendix
MotorVAR + Reactor Calculation Method Summary
Isc: 1.2kA
[7 empty] | 34.5kV Bus |  | X/R: 7
40 MVA
7.5%
12.47kV Bus
Line Reactor
1.64 ohms
[12 empty] | BYPASS |  |  | X/R:100
9,923HP, 12.47kV
LRA: 500%
FLA: 351.9A
[10 empty] | Voltage change per stage at the 12.47 kV Bus: | [8 empty] | ±4.95%
Disclaimer and Use Limitation
|  |  |  | MotorVAR System | [8 empty] | Legend: | [8 empty] | This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
|  |  |  | 12.47KV, 25 MVAR | [8 empty] | Red: Across the line start, no assistance
|  |  |  | 4 Stage MotorVAR | [8 empty] | Light Blue: MotorVAR with (reactor bypassed)
Dark Blue: MotorVAR + Reactor Assisted
| Info@VarStec.com | [19 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [6 empty] | 6 ¦ P a g e
MotorVAR™ SIZING TOOL, MotorVar ¦ REACTOR-ASSISTED MOTOR START SYSTEM | [21 empty] | MotorVAR™ SIZING TOOL, MotorVar ¦ REACTOR-ASSISTED MOTOR START SYSTEM
| Info@VarStec.com | [19 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [6 empty] | 8 ¦ P a g e
39.1%
96.5%
84.5%
This spreadsheet provides preliminary sizing and voltage-performance evaluation of VarStec’s MotorVAR + Line Reactor solution for large medium-voltage motor starting. It models a simplified system including the utility source, transformer, motor bus with MotorVAR support, and a series line reactor. The tool determines the required line reactor impedance (ohms) and MotorVAR reactive power needed to meet voltage-performance targets during motor starting. Inputs such as utility short-circuit strength, transformer data, motor parameters, and reactor impedance enable rapid iteration to limit inrush current while maintaining acceptable bus and motor terminal voltage. This worksheet extends the MotorVAR-only analysis by explicitly accounting for the combined effects of reactive support and reactor current limiting effect on motor-starting performance.
Without MotorVAR or reactor start assistance, the motor draws approximately 1099.8 amps (312.5% of FLA) during starting. This high inrush current results in a significant voltage drop, with motor terminal voltage dropping to approximately 7.79 kV, or 62.5% of rated voltage. As a result, available starting torque is reduced to roughly 39.1% of rated torque, increasing the likelihood of extended acceleration times or a stalled start condition. From a system perspective, voltage at the 34.5 kV PCC drops to approximately 23.08 kV, or 66.9% of nominal, while the 12.47 kV secondary bus voltage falls to 7.79 kV, or 62.5% of rated voltage. These correspond to voltage drops of 33.1% at the PCC and 37.5% at the secondary bus. Typical design objectives require no less than 96% voltage at the PCC and 90% voltage at the motor bus during starting. When these criteria are not met, alternative starting methods are usually evaluated.
When adding a coordinated line reactor, the combined MotorVAR + Reactor system provides additional improvement in overall system performance compared to a MotorVAR-only solution. During motor starting, the 34.5 kV bus voltage improves from 84.5% to 96.5% of nominal, while the 12.47kV bus voltage improves from 82.6% to 96.2%. This improvement is driven by the current-limiting action of the line reactor (1.64 ohms). While current limiting improves voltage performance, it also reduces the current delivered to the motor and, consequently, the available starting torque. In this case, motor starting torque is reduced from 68.2% with MotorVAR only to approximately 47.5% with the combined MotorVAR + Reactor system. It is therefore critical to verify that the available starting torque remains sufficient to accelerate the driven load under all expected starting conditions.
This analysis evaluates the starting performance of a 9,923 HP, 12.47 kV motor supplied from a 34.5 kV utility system at the point of common coupling (PCC). The available utility short-circuit strength at the PCC is 1.2 kA (3-phase) with an X/R ratio of 7, feeding the motor through a 40 MVA, 34.5 kV–12.47 kV step-down transformer with 7.5% leakage impedance. The motor has a full-load current (FLA) of 351.9 amps, a locked-rotor current (LRA) of 500% of FLA, a rated efficiency of 97.4%, and a power factor of 90%. To enhance starting performance and mitigate system disturbances, a starting reactor rated at 1.64 ohms is coordinated with a 25 MVAR, 12.47 kV, 4-stage MotorVAR system to provide controlled, high-performance starting assistance.
With the MotorVAR system engaged and line reactor out of service or bypassed, the motor starting performance improves significantly. Motor starting current increases to approximately 1453.5 amps (413% of FLA), while motor terminal voltage is maintained near 10.3 kV, or 82.6% of rated voltage. This allows the motor to develop approximately 68.2% of rated torque during starting, resulting in stronger acceleration and improved starting stability. System voltage performance is also significantly improved. Voltage at the 34.5kV PCC and the 12.5kV secondary bus are maintained at approximately 96.5% and 96.2% of nominal, respectively. The starting current reflected into the 34.5kV and 12.5kV systems is reduced to approximately 156.3 %FLA, substantially mitigating upstream system disturbances. As the motor transitions into synchronism, the 4 stage MotorVAR system limits the voltage fluctuations to approximately ±4.95%% of the nominal voltage at the 12.5kV bus.
MotorVAR delivers fast, localized reactive power exactly where it is needed—at the motor bus—fundamentally improving the way large medium-voltage motors are started. It can be applied independently or coordinated with other starting methods, such as RVSS or reactor-start systems, to extend their effective range and further improve performance. By actively supporting voltage during acceleration, MotorVAR mitigates voltage sag, improves power quality, and preserves starting torque, enabling the use of simple across-the-line starting without compromising system performance or plant reliability.
The MotorVAR system seamlessly coordinates with a wide range of motor-starting solutions. It is a high-speed, switched capacitor bank designed to be transient-free during both energization and de-energization. This approach eliminates the complexity, footprint, and operational burden typically associated with ASD/VFD solutions, synchronous bypass switchgear, E-house requirements, and the extended startup, commissioning, and lifecycle costs that accompany those systems.
A single MotorVAR installation can support multiple large motors on the same electrical system, often eliminating the need for dedicated starting equipment at each motor. Shared or cross-tie starting configurations can further improve project economics. The result is a robust, practical motor-starting solution that minimizes system disturbance while significantly reducing project complexity, cost, and risk.
This spreadsheet implements a steady-state impedance model to estimate motor starting current, voltage sag, and available starting torque for a simplified medium-voltage motor starting system. All calculations are performed per phase using complex impedances.
The modeled system consists of a utility source at the point of common coupling (PCC), source impedance , transformer impedance , a secondary bus that also serves as the motor bus, an optional series line reactor , and an induction motor represented by its locked-rotor impedance . A MotorVAR capacitor bank is modeled as a shunt capacitive reactance connected at the secondary bus. No additional line or cable impedance between the bus and motor is assumed. The motor rated voltage may differ from the secondary bus voltage.
Complex impedances are expressed as: . Line-to-line and phase voltages are related by: . The total upstream impedance is defined as: . Motor starting torque is approximated using the square-law voltage relationship: . Baseline Case (No MotorVAR, No Reactor) The motor is connected directly to the secondary bus through the upstream impedance. The equivalent load impedance is: . System and motor current: . Secondary bus and motor terminal voltage: . This case establishes baseline inrush current, voltage sag, and starting torque.
MotorVAR-Only Case (Reactor Bypassed) The MotorVAR capacitor bank is connected in parallel with the motor at the secondary bus. The capacitor impedance is: . The equivalent bus impedance is: . System current and bus voltage: . . Branch currents: . Motor terminal voltage equals the bus voltage. System inrush current, motor inrush current, voltage sag, and starting torque are evaluated. MotorVAR + Line Reactor Case The MotorVAR capacitor remains connected at the secondary bus while a line reactor is inserted in series with the motor. The motor branch impedance becomes: . The equivalent bus impedance is: . System current: and bus voltage: . Motor branch current: . Motor terminal voltage: .
This spreadsheet implements a steady-state impedance model to estimate motor starting current, voltage sag, and available starting torque for a simplified medium-voltage motor starting system. All calculations are performed per phase using complex impedances.
The modeled system consists of a utility source at the point of common coupling (PCC), source impedance 𝑍_𝑆, transformer impedance 𝑍_𝑇, a secondary bus that also serves as the motor bus, an optional series line reactor 𝑍_𝑅, and an induction motor represented by its locked-rotor impedance 𝑍_𝑀. A MotorVAR capacitor bank is modeled as a shunt capacitive reactance connected at the secondary bus. No additional line or cable impedance between the bus and motor is assumed. The motor rated voltage may differ from the secondary bus voltage.
Complex impedances are expressed as: 𝑍=𝑅+𝑗𝑋. Line-to-line and phase voltages are related by: 𝑉_𝑝ℎ=𝑉_𝐿𝐿/√3. The total upstream impedance is defined as: 𝑍_𝑢𝑝=𝑍_𝑆+𝑍_𝑇. Motor starting torque is approximated using the square-law voltage relationship: 𝑇_(𝑠𝑡𝑎𝑟𝑡,%)≈100%((∣𝑉_(𝑀,𝐿𝐿)∣)/𝑉_(𝑀,𝑟𝑎𝑡𝑒𝑑,𝐿𝐿) )^2. Baseline Case (No MotorVAR, No Reactor) The motor is connected directly to the secondary bus through the upstream impedance. The equivalent load impedance is: 𝑍_𝑒𝑞=𝑍_𝑀. System and motor current: 𝐼_𝑃𝐶𝐶=𝐼_𝑀=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑢𝑝+𝑍_𝑀 ). Secondary bus and motor terminal voltage: 𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑀,𝑝ℎ)=𝐼_𝑀 𝑍_𝑀. This case establishes baseline inrush current, voltage sag, and starting torque.
MotorVAR-Only Case (Reactor Bypassed) The MotorVAR capacitor bank is connected in parallel with the motor at the secondary bus. The capacitor impedance is: 𝑍_𝐶=−𝑗 (𝑉_(𝑆,𝐿𝐿)^2)/𝑄_𝑀𝑉 . The equivalent bus impedance is: 𝑍_𝑒𝑞=𝑍_𝑀∥𝑍_𝐶. System current and bus voltage: 𝐼_𝑃𝐶𝐶=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑢𝑝+𝑍_𝑒𝑞 ). 𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ) 𝑍_𝑒𝑞/(𝑍_𝑢𝑝+𝑍_𝑒𝑞 ). Branch currents: 𝐼_𝑀=𝑉_(𝑆,𝑝ℎ)/𝑍_𝑀 ,𝐼_𝐶=𝑉_(𝑆,𝑝ℎ)/𝑍_𝐶 . Motor terminal voltage equals the bus voltage. System inrush current, motor inrush current, voltage sag, and starting torque are evaluated. MotorVAR + Line Reactor Case The MotorVAR capacitor remains connected at the secondary bus while a line reactor is inserted in series with the motor. The motor branch impedance becomes: 𝑍_𝑀𝑅=𝑍_𝑅+𝑍_𝑀. The equivalent bus impedance is: 𝑍_𝑒𝑞=𝑍_𝑀𝑅∥𝑍_𝐶. System current: 𝐼_𝑃𝐶𝐶=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ)/(𝑍_𝑢𝑝+𝑍_𝑒𝑞 ) and bus voltage: 𝑉_(𝑆,𝑝ℎ)=𝑉_(𝑠𝑜𝑢𝑟𝑐𝑒,𝑝ℎ) 𝑍_𝑒𝑞/(𝑍_𝑢𝑝+𝑍_𝑒𝑞 ). Motor branch current: 𝐼_𝑀=𝑉_(𝑆,𝑝ℎ)/(𝑍_𝑅+𝑍_𝑀 ). Motor terminal voltage: 𝑉_(𝑀,𝑝ℎ)=𝑉_(𝑆,𝑝ℎ)−𝐼_𝑀 𝑍_𝑅.
66.9%
96.2%
82.6%
62.5%
47.5%
68.2%
Voltage During Start
Voltage During Start
312.5%
55.9%
156.3%
Current During Start (%FLA)
(%FLA)
312.5%
344.7%
413.0%
Source
Motor
0
1114
957
Current Assist from MotorVAR (amps)
% Torque During Start
(amps)
1213
1454
1100
One-line diagram showing analysis results for three system configurations: the first, shown in red text, represents operation with no assistance from either the MotorVAR or the line reactor, the second, shown in light blue, represents the MotorVAR-only case with the line reactor bypassed; and the third, shown in dark blue, represents operation with both the MotorVAR + Reactor in service.
Starting Current
Step-Down Transformer
Step-Down Transformer
Source
M
Controls
Controls