## Overview and Purpose
VarStec Power Solutions, Inc.
PO Box 942
|  |  | Saratoga Springs, NY 12866 | Harmonic Filter Design Workbook, Overview and Purpose
518.369.7589
Harmonic Filter Design Workbook Overview and Purpose
[6 empty] | Notch Filter | High-Pass Filter | C-High-Pass Filter
| Info@VarStec.com |  |  |  | Info@VarStec.com |  |  |  | 2 ¦ P a g e
Sheet Rev Date: 1-11-2026
Overview
VarStec’s Harmonic Filter Design Workbook is an engineering tool developed to support the design, evaluation, and comparison of medium-voltage harmonic filter systems used in industrial, utility, and renewable power networks. The workbook provides a consistent, transparent methodology for designing single-tuned (notch), high-pass (HP), and C-high-pass (C-HP) harmonic filters based on fundamental system requirements and known harmonic current spectra.
Harmonic filters are applied to mitigate voltage distortion, limit harmonic current propagation, suppress resonance, and provide reactive power support in systems containing non-linear loads such as large variable-speed drives, rectifiers, soft starters, and other power electronic equipment. Proper filter design requires careful coordination of tuning, reactive power rating, component voltage and current duty ratings, and proper rating of filter components. Inadequate or poorly coordinated filter designs can result in excessive capacitor stress, resonance amplification, overheating, and premature failure of the filter.
This workbook models harmonic filters using established electrical relationships and industry-accepted practices. All calculations are performed using explicit reactance-based formulations, allowing the engineer to clearly trace how tuning, capacitance, inductance, damping, and harmonic current injection influence filter component ratings. The workbook does not rely on proprietary algorithms, black-box solvers, or embedded harmonic simulation engines. Instead, it assumes that harmonic current spectra have been developed separately through system studies or measurements and are provided as inputs to the design.
By maintaining a fully transparent calculation framework, the workbook enables qualified engineers to independently verify results, perform sensitivity checks, and adapt designs to project-specific requirements. The tool is intended to assist with filter design and specification and to support engineers performing harmonic studies.
Workbook Purpose
This workbook is intended to support the preliminary sizing, tuning, and verification of medium-voltage harmonic filters engineered by VarStec Power Solutions. It provides a structured framework for evaluating filter performance, component duty, and losses across multiple commonly applied filter topologies. Each worksheet represents a specific filter configuration and is used to determine appropriate capacitor, reactor, and damping resistor ratings that satisfy defined harmonic mitigation and system performance objectives.
The workbook supports both forward design and reverse engineering use cases. Forward-design worksheets are used to develop complete filter designs from system requirements (system voltage and frequency, reactive power requirements, current injection data, tuning point, and damping factor), while reverse-calculator tools are provided to back-calculate key filter ratings to allow for the use of the forward design worksheets.
Notch Filter Design
This worksheet supports the forward design of a classical single-tuned (notch) harmonic filter. The fundamental reactive power rating and tuning point are defined, and the corresponding capacitor and reactor reactances are calculated. Injected harmonic currents are applied to evaluate capacitor voltage stress, current duty, reactive power duty, reactor current loading, and overall filter impedance characteristics. The notch filter design is typically the most economical solution and is widely applied where harmonic mitigation, power factor correction, and resonance control can be achieved without the use of damping resistors.
High-Pass (HP) Filter Design
This worksheet extends the notch filter methodology by incorporating a damping resistor to provide broadband harmonic attenuation above the tuning frequency. In addition to capacitor and reactor sizing, the tool evaluates damping factor, resistor current, and resistor power dissipation under both fundamental and harmonic conditions.
High-pass filters are typically applied where interharmonics, system capacitance, or multiple resonance points require damping. The worksheet explicitly accounts for the increased losses associated with resistive damping and is used to determine whether a high-pass or alternative topology is more appropriate.
C-High-Pass (C-HP) Filter Design
This worksheet supports the design of a classical C-high-pass harmonic filter, which incorporates an auxiliary capacitor tuned with the reactor to eliminate fundamental-frequency losses in the damping resistor. This topology allows for very low damping factors while maintaining negligible fundamental losses (50 or 60 Hertz), making it suitable for systems with high harmonic energy or aggressive damping requirements.
The worksheet independently evaluates the main and auxiliary capacitor groups, reactor loading, damping resistor performance, harmonic current distribution, and total losses, providing a complete assessment of C-HP filter design.
Reverse Calculator Tools
The workbook includes reverse-calculation worksheets for Notch, High-Pass, and C-High-Pass filter topologies. These tools are used when filter inductance, capacitance, and damping resistance are already defined, such as when evaluating existing installations, customer or EPC supplied component ratings, or legacy designs with incomplete documentation.
The reverse calculators back-calculate tuning frequency, reactive power rating, and damping factor. Three key inputs for the forward design worksheets (notch, High-Pass, and C-High-Pass worksheets). With the key inputs, the forward design worksheets may be employed.
Intended Use This workbook is intended for use by qualified electrical engineers familiar with medium-voltage power systems and harmonic analysis. It is designed to support early-stage engineering, option screening, and design validation and should be used in conjunction with system harmonic studies, protection coordination, and applicable IEEE and IEC standards.
For additional information, engineering support, or custom harmonic filter designs, contact VarStec Power Solutions at info@varstec.com.

## Notch Filter Design
[58 empty] | IMPEDANCE TABLE | [22 empty] | X
[34 empty] | VarStec Power Solutions, Inc. | [24 empty] | PLOT (ohms) |  |  |  |  | (aux branch) | (Resistance Branch) X (Aux Branch) | RES Branch + Aux branch | Parallel Sum of Aux and Resistance Branch | + Main Cap | [14 empty] | SD - Standard Duty Capacitors
[34 empty] | PO Box 942 | [23 empty] | HARM # | Xc | No Aux… rounded to 0 | XL | Resistance set to infinite |  | Xc+XL | [18 empty] | HD- Heavy Duty Capacitors
[34 empty] | Saratoga Springs, NY 12866 | Enter Customer PO # ¦ Stage 1 | [22 empty] | 1 | 0.0001-26.996684i | 0.000000001 | 0.010799+1.079867i | 5399336805.55556+0.0001i |  | 0.010799001+1.079867i | 58307443.562423+5830565638.20487i | 5399336805.56636+1.079967i | 0.010799+1.079867i | 0.010899-25.916817i |  | 1 | 417.1862 | 174044.3405 | [8 empty] | 1 | 25.9168 | EXD - Extreme Duty Capacitors
[34 empty] | 518.369.7589 | [23 empty] | 1.2 | 0.0001-22.497237i | 0.000000001 | 0.010799+1.295841i | 5399336805.55556+0.0001i |  | 0.010799001+1.295841i | 58307443.562402+6996682005.44792i | 5399336805.56636+1.295941i | 0.010799+1.295841i | 0.010899-21.201396i |  | 2 | 0 | 0 | [8 empty] | 1.2 | 21.2014
| Harmonic Filter Design / Notch Type | [33 empty] | 📐 DESIGN VERIFICATION | [22 empty] | 1.4 | 0.0001-19.283346i | 0.000000001 | 0.010799+1.511814i | 5399336805.55556+0.0001i |  | 0.010799001+1.511814i | 58307443.56238+8162792973.35417i | 5399336805.56636+1.511914i | 0.010799+1.511814i | 0.010899-17.771532i |  | 3 | 0 | 0 | [8 empty] | 1.4 | 17.7715 | DF (Damping Factor) | 300
[58 empty] | 1.6 | 0.0001-16.872928i | 0.000000001 | 0.010799+1.727788i | 5399336805.55556+0.0001i |  | 0.010799001+1.727788i | 58307443.562359+9328909340.59723i | 5399336805.56636+1.727888i | 0.010799+1.727788i | 0.010899-15.14514i |  | 4 | 0 | 0 | [8 empty] | 1.6 | 15.1451
| 📜 PROJECT DETAILS | [31 empty] | April 19, 2026 |  | Capacitor Design Ratings Versus Duty Rating | [22 empty] | 1.8 | 0.0001-14.998158i | 0.000000001 | 0.010799+1.943761i | 5399336805.55556+0.0001i |  | 0.010799001+1.943761i | 58307443.562337+10495020308.5035i | 5399336805.56636+1.943861i | 0.010799+1.943761i | 0.010899-13.054397i |  | 5 | 150 | 22500 | [8 empty] | 1.8 | 13.0544
[41 empty] | Design Values | [16 empty] | 2 | 0.0001-13.498342i | 0.000000001 | 0.010799+2.159735i | 5399336805.55556+0.0001i |  | 0.010799001+2.159735i | 58307443.562315+11661136675.7465i | 5399336805.56636+2.159835i | 0.010799+2.159735i | 0.010899-11.338607i |  | 7 | 120 | 14400 | [8 empty] | 2 | 11.3386
|  |  |  | Project Name: | Enter Project Name | [17 empty] | VarStec SO #: |  | Enter SO Number | [15 empty] | At Nominal Voltage | [6 empty] | At Nominal 110% System Voltage | [9 empty] | 2.2 | 0.0001-12.27122i | 0.000000001 | 0.010799+2.375708i | 5399336805.55556+0.0001i |  | 0.010799001+2.375708i | 58307443.562294+12827247643.6528i | 5399336805.56636+2.375808i | 0.010799+2.375708i | 0.010899-9.895512i |  | 11 | 90 | 8100 | [8 empty] | 2.2 | 9.8955
|  |  |  | Customer PO #: | Enter Customer PO # | [17 empty] | Revision #: |  | Rev 1 - | [10 empty] | Design Parameter | [12 empty] | Rated Duty | [8 empty] | 2.4 | 0.0001-11.248618i | 0.000000001 | 0.010799+2.591682i | 5399336805.55556+0.0001i |  | 0.010799001+2.591682i | 58307443.562272+13993364010.8958i | 5399336805.56636+2.591782i | 0.010799+2.591682i | 0.010899-8.656936i |  | 13 | 45 | 2025 | [8 empty] | 2.4 | 8.6569
|  |  |  | Tag #: | Enter Tag Number | [17 empty] | Stage/Branch: |  | Stage 1 | [14 empty] | % RATED VOLTS: | 75.66% | [6 empty] | 83.18% | 125% | [8 empty] | 2.6 | 0.0001-10.38334i | 0.000000001 | 0.010799+2.807655i | 5399336805.55556+0.0001i |  | 0.010799001+2.807655i | 58307443.562251+15159474978.8021i | 5399336805.56636+2.807755i | 0.010799+2.807655i | 0.010899-7.575685i |  | 17 | 30 | 900 | [8 empty] | 2.6 | 7.5757
[40 empty] | % CREST VOLTAGE: | 86.85% | [6 empty] | 96.85% | 135% | [8 empty] | 2.8 | 0.0001-9.641673i | 0.000000001 | 0.010799+3.023629i | 5399336805.55556+0.0001i |  | 0.010799001+3.023629i | 58307443.562229+16325591346.0452i | 5399336805.56636+3.023729i | 0.010799+3.023629i | 0.010899-6.618044i |  | 19 | 15 | 225 | [8 empty] | 2.8 | 6.6181
| 🧮 SPECIFICATION DETAILS | [38 empty] | % 60HZ AMPS: | 85.35% | [6 empty] | 92.08% | 135% | [8 empty] | 3 | 0.0001-8.998895i | 0.000000001 | 0.010799+3.239602i | 5399336805.55556+0.0001i |  | 0.010799001+3.239602i | 58307443.562207+17491702313.9514i | 5399336805.56636+3.239702i | 0.010799+3.239602i | 0.010899-5.759293i |  | 23 | 15 | 225 | [8 empty] | 3 | 5.7593
|  | Key Filter Ratings | [37 empty] | % 60HZ KVAR: | 59.29% | [6 empty] | 71.23% | 135% | [8 empty] | 3.2 | 0.0001-8.436464i | 0.000000001 | 0.010799+3.455576i | 5399336805.55556+0.0001i |  | 0.010799001+3.455576i | 58307443.562186+18657818681.1945i | 5399336805.56636+3.455676i | 0.010799+3.455576i | 0.010899-4.980888i |  | 25 | 15 | 225 | [8 empty] | 3.2 | 4.9809 |  |  |  | DF (Damping Factor of High-Pass Filter): |  |  | 1000000000
[13 empty] | kVLLsys (System Line-to-Line Voltage Rating): | 12.47 |  |  | kV | [11 empty] | Xeff Filter Effective Reactance): | 25.9168 |  |  | Ohms | [24 empty] | 3.4 | 0.0001-7.940201i | 0.000000001 | 0.010799+3.671549i | 5399336805.55556+0.0001i |  | 0.010799001+3.671549i | 58307443.562164+19823929649.1007i | 5399336805.56636+3.671649i | 0.010799+3.671549i | 0.010899-4.268652i |  | 29 | 0 | 0 | [8 empty] | 3.4 | 4.2687 |  |  | High-Pass Resistor Losses: |  | 0.0010871 | Watts, 3-Phase or 0 BTUs/Hour
|  |  | Qeff (3-Phase Output Rating of Filter): | [10 empty] | 6000 |  |  | kvar | [17 empty] | ICAP (Fundamental Current per Capacitor): | [8 empty] | 55.6248 |  |  | amps |  |  | Capacitive Reactance (per can): | 134.9834 | Ohms | [5 empty] | 3.6 | 0.0001-7.499079i | 0.000000001 | 0.010799+3.887523i | 5399336805.55556+0.0001i |  | 0.010799001+3.887523i | 58307443.562143+20990046016.3438i | 5399336805.56636+3.887623i | 0.010799+3.887523i | 0.010899-3.611556i |  | 31 | 0 | 0 | [8 empty] | 3.6 | 3.6116
|  |  | hn (Tuning Point of Filter): | [10 empty] | 5 |  |  | (harmonic number) | [11 empty] | hf : | 300 |  |  | Hz |  | I CAP FUSE (Minimum Fuse Rating): | [8 empty] | 100.1247 |  |  | amps |  |  | Capacitance (per can): | 19.6518 | µF | [5 empty] | 3.8 | 0.0001-7.104391i | 0.000000001 | 0.010799+4.103496i | 5399336805.55556+0.0001i |  | 0.010799001+4.103496i | 58307443.562121+22156156984.25i | 5399336805.56636+4.103596i | 0.010799+4.103496i | 0.010899-3.000895i |  | 35 | 15 | 225 | [8 empty] | 3.8 | 3.0009
|  |  | f (System Frequency): | [10 empty] | 60 |  |  | (HZ) | [11 empty] | IRATED FUNDAMENTAL: | 278.1241 |  |  | amps |  | VCAP FUNDAMENTAL VOLTAGE: | [8 empty] | 7.5084 |  |  | kV | [10 empty] | 4 | 0.0001-6.749171i | 0.000000001 | 0.010799+4.319469i | 5399336805.55556+0.0001i |  | 0.010799001+4.319469i | 58307443.562099+23322267952.1563i | 5399336805.56636+4.319569i | 0.010799+4.319469i | 0.010899-2.429702i |  | 37 | 15 | 225 | [8 empty] | 4 | 2.4297
[29 empty] | IFILTER RMS CURRENT: | 314.8858 |  |  | amps |  | VCAP RMS VOLTAGE: | [8 empty] | 7.536 |  |  | kV | [10 empty] | 4.2 | 0.0001-6.427782i | 0.000000001 | 0.010799+4.535443i | 5399336805.55556+0.0001i |  | 0.010799001+4.535443i | 58307443.562078+24488384319.3993i | 5399336805.56636+4.535543i | 0.010799+4.535443i | 0.010899-1.892339i |  |  |  | 472.3286 | [8 empty] | 4.2 | 1.8924
[35 empty] | VCAP, PEAK CAP VOLTAGE: | [8 empty] | 12.2311 |  |  | kV | [10 empty] | 4.4 | 0.0001-6.13561i | 0.000000001 | 0.010799+4.751416i | 5399336805.55556+0.0001i |  | 0.010799001+4.751416i | 58307443.562056+25654495287.3056i | 5399336805.56636+4.751516i | 0.010799+4.751416i | 0.010899-1.384194i | [12 empty] | 4.4 | 1.3842
| Expected Harmonic Current (amps) Into Line Side of Filter of Filter Branch/Stage | [33 empty] | ICAP RMS CURRENT: | [8 empty] | 62.9772 |  |  | amps | [10 empty] | 4.6 | 0.0001-5.868844i | 0.000000001 | 0.010799+4.96739i | 5399336805.55556+0.0001i |  | 0.010799001+4.96739i | 58307443.562035+26820611654.5486i | 5399336805.56636+4.96749i | 0.010799+4.96739i | 0.010899-0.901454i | [12 empty] | 4.6 | 0.90152
| (n) Harmonic: | [5 empty] | 1 | 2 |  | 3 |  | 4 | 5 |  | 7 |  | 11 |  | 13 | 17 |  | 19 |  | 23 |  | 25 | 29 |  | 31 |  | 35 |  | 37 |  | QCAPACITOR (1-phase): | [8 empty] | 2178.8087 |  |  | kvar | [10 empty] | 4.8 | 0.0001-5.624309i | 0.000000001 | 0.010799+5.183363i | 5399336805.55556+0.0001i |  | 0.010799001+5.183363i | 58307443.562013+27986722622.4549i | 5399336805.56636+5.183463i | 0.010799+5.183363i | 0.010899-0.440946i | [12 empty] | 4.8 | 0.44108
| (In) Filter current: | [5 empty] | 278.1241 | 0 |  | 0 |  | 0 | 100 |  | 80 |  | 60 |  | 30 | 20 |  | 10 |  | 10 |  | 10 | 0 |  | 0 |  | 10 |  | 10 | [24 empty] | 5 | 0.0001-5.399337i | 0.000000001 | 0.010799+5.399337i | 5399336805.55556+0.0001i |  | 0.010799001+5.399337i | 58307443.561991+29152838989.6979i | 5399336805.56636+5.399437i | 0.010799+5.399337i | 0.010899 | [12 empty] | 5 | 0.010899
[58 empty] | 5.2 | 0.0001-5.19167i | 0.000000001 | 0.010799+5.61531i | 5399336805.55556+0.0001i |  | 0.010799001+5.61531i | 58307443.56197+30318949957.6042i | 5399336805.56636+5.61541i | 0.010799+5.61531i | 0.010899+0.42364i | [12 empty] | 5.2 | 0.42378
| Capacitor Rating Details | [56 empty] | 5.4 | 0.0001-4.999386i | 0.000000001 | 0.010799+5.831284i | 5399336805.55556+0.0001i |  | 0.010799001+5.831284i | 58307443.561948+31485066324.8472i | 5399336805.56636+5.831384i | 0.010799+5.831284i | 0.010899+0.831898i | [12 empty] | 5.4 | 0.83197
VCAP RATING (Voltage Rating of Capacitor): | [13 empty] | 9.96 |  |  | kV | [10 empty] | Individual Capacitor Rating: | 734.9169 |  |  | kvar | [25 empty] | 5.6 | 0.0001-4.820836i | 0.000000001 | 0.010799+6.047257i | 5399336805.55556+0.0001i |  | 0.010799001+6.047257i | 58307443.561927+32651177292.7535i | 5399336805.56636+6.047357i | 0.010799+6.047257i | 0.010899+1.226421i | [12 empty] | 5.6 | 1.2265
N (Number of Capacitors Per Phase): | [13 empty] | 5 | [13 empty] | Q RATED PER PHASE: | 3674.5846 |  |  | kvar | [25 empty] | 5.8 | 0.0001-4.654601i | 0.000000001 | 0.010799+6.263231i | 5399336805.55556+0.0001i |  | 0.010799001+6.263231i | 58307443.561905+33817293659.9966i | 5399336805.56636+6.263331i | 0.010799+6.263231i | 0.010899+1.60863i | [12 empty] | 5.8 | 1.6087
[7 empty] | HD- Heavy Duty Capacitors | [20 empty] | XC: | 26.9967 |  |  | Ohms | [25 empty] | 6 | 0.0001-4.499447i | 0.000000001 | 0.010799+6.479204i | 5399336805.55556+0.0001i |  | 0.010799001+6.479204i | 58307443.561883+34983404627.9028i | 5399336805.56636+6.479304i | 0.010799+6.479204i | 0.010899+1.979757i | [12 empty] | 6 | 1.9798
[28 empty] | Capacitor Capacitance (per phase): | 98.26 |  |  | 𝜇F/Phase | [25 empty] | 6.2 | 0.0001-4.354304i | 0.000000001 | 0.010799+6.695178i | 5399336805.55556+0.0001i |  | 0.010799001+6.695178i | 58307443.561862+36149520995.1459i | 5399336805.56636+6.695278i | 0.010799+6.695178i | 0.010899+2.340874i | [12 empty] | 6.2 | 2.3409
[58 empty] | 6.4 | 0.0001-4.218232i | 0.000000001 | 0.010799+6.911151i | 5399336805.55556+0.0001i |  | 0.010799001+6.911151i | 58307443.56184+37315631963.0521i | 5399336805.56636+6.911251i | 0.010799+6.911151i | 0.010899+2.692919i | [12 empty] | 6.4 | 2.6929
| Tuning Reactor | [56 empty] | 6.6 | 0.0001-4.090407i | 0.000000001 | 0.010799+7.127125i | 5399336805.55556+0.0001i |  | 0.010799001+7.127125i | 58307443.561819+38481748330.2952i | 5399336805.56636+7.127225i | 0.010799+7.127125i | 0.010899+3.036718i | [12 empty] | 6.6 | 3.0367
| X/Rratio (Tuning Reactor at System Frequency): | [12 empty] | 100 |  |  |  | XL (Inductive Reactance): | [10 empty] | 1.0799 |  |  | ohms | [25 empty] | 6.8 | 0.0001-3.970101i | 0.000000001 | 0.010799+7.343098i | 5399336805.55556+0.0001i |  | 0.010799001+7.343098i | 58307443.561797+39647859298.2014i | 5399336805.56636+7.343198i | 0.010799+7.343098i | 0.010899+3.372997i | [12 empty] | 6.8 | 3.373
[13 empty] | Enter Fundamental Current Design Margin: | 1.5 |  |  | HL (Inductance): | [11 empty] | 2.8645 |  |  | mH | [25 empty] | 7 | 0.0001-3.856669i | 0.000000001 | 0.010799+7.559072i | 5399336805.55556+0.0001i |  | 0.010799001+7.559072i | 58307443.561775+40813975665.4445i | 5399336805.56636+7.559172i | 0.010799+7.559072i | 0.010899+3.702403i | [12 empty] | 7 | 3.7024 | [7 empty] | High-Pass Resistor
[13 empty] | Enter Harmonic Current Design Margin: | 1.5 | [43 empty] | 7.2 | 0.0001-3.749539i | 0.000000001 | 0.010799+7.775045i | 5399336805.55556+0.0001i |  | 0.010799001+7.775045i | 58307443.561754+41980086633.3507i | 5399336805.56636+7.775145i | 0.010799+7.775045i | 0.010899+4.025506i | [12 empty] | 7.2 | 4.0255 | [11 empty] | Rw (Resistor KW/Phase - Specified): | 5.686e-07 | kW/Phase
[58 empty] | 7.4 | 0.0001-3.648201i | 0.000000001 | 0.010799+7.991018i | 5399336805.55556+0.0001i |  | 0.010799001+7.991018i | 58307443.561732+43146197601.257i | 5399336805.56636+7.991118i | 0.010799+7.991018i | 0.010899+4.342817i | [12 empty] | 7.4 | 4.3428 | [9 empty] | Ifundamental resistor current (actual): | 2.6496e-07 | amps |  |  |  |  | R (Resistor Ohm rating/phase): | 5399336805.5556 | Ohms
[58 empty] | 7.6 | 0.0001-3.552195i | 0.000000001 | 0.010799+8.206992i | 5399336805.55556+0.0001i |  | 0.010799001+8.206992i | 58307443.561711+44312313968.5i | 5399336805.56636+8.207092i | 0.010799+8.206992i | 0.010899+4.654797i | [12 empty] | 7.6 | 4.6548 | [9 empty] | Ifundamental resistor current (specified): | 3.2451e-07 | amps |  |  |  |  | (Rw) (Resistor KW/phase, actual): | 3.7907e-07 | kW/Phase
[58 empty] | 7.8 | 0.0001-3.461113i | 0.000000001 | 0.010799+8.422965i | 5399336805.55556+0.0001i |  | 0.010799001+8.422965i | 58307443.561689+45478424936.4063i | 5399336805.56636+8.423065i | 0.010799+8.422965i | 0.010899+4.961852i | [12 empty] | 7.8 | 4.9619
[58 empty] | 8 | 0.0001-3.374586i | 0.000000001 | 0.010799+8.638939i | 5399336805.55556+0.0001i |  | 0.010799001+8.638939i | 58307443.561667+46644541303.6493i | 5399336805.56636+8.639039i | 0.010799+8.638939i | 0.010899+5.264353i | [12 empty] | 8 | 5.2644 | [16 empty] | IRESISTOR CURRENT (amps)
[58 empty] | 8.2 | 0.0001-3.292279i | 0.000000001 | 0.010799+8.854912i | 5399336805.55556+0.0001i |  | 0.010799001+8.854912i | 58307443.561646+47810652271.5556i | 5399336805.56636+8.855012i | 0.010799+8.854912i | 0.010899+5.562633i | [12 empty] | 8.2 | 5.5626
[81 empty] | 8.4 | 5.857 | [16 empty] | 5.5625e-08
[81 empty] | 8.6 | 6.1477 | [16 empty] | 0
[58 empty] | 8.4 | 0.0001-3.213891i | 0.000000001 | 0.010799+9.070886i | 5399336805.55556+0.0001i |  | 0.010799001+9.070886i | 58307443.561624+48976768638.7987i | 5399336805.56636+9.070986i | 0.010799+9.070886i | 0.010899+5.856995i | [12 empty] | 8.8 | 6.435 | [16 empty] | 0
[58 empty] | 8.6 | 0.0001-3.139149i | 0.000000001 | 0.010799+9.286859i | 5399336805.55556+0.0001i |  | 0.010799001+9.286859i | 58307443.561603+50142879606.7049i | 5399336805.56636+9.286959i | 0.010799+9.286859i | 0.010899+6.14771i | [12 empty] | 9 | 6.7192 | [16 empty] | 0
[58 empty] | 8.8 | 0.0001-3.067805i | 0.000000001 | 0.010799+9.502833i | 5399336805.55556+0.0001i |  | 0.010799001+9.502833i | 58307443.561581+51308995973.948i | 5399336805.56636+9.502933i | 0.010799+9.502833i | 0.010899+6.435028i | [12 empty] | 9.2 | 7.0004 | [16 empty] | 1e-07
[81 empty] | 9.4 | 7.2788 | [16 empty] | 1.12e-07
|  | Info@VarStec.com | [31 empty] | Rev Date: 4-19-2026 |  | Info@VarStec.com | [16 empty] | 2 ¦ P a g e |  |  |  |  | 9 | 0.0001-2.999632i | 0.000000001 | 0.010799+9.718806i | 5399336805.55556+0.0001i |  | 0.010799001+9.718806i | 58307443.561559+52475106941.8542i | 5399336805.56636+9.718906i | 0.010799+9.718806i | 0.010899+6.719174i | [12 empty] | 9.6 | 7.5546 | [16 empty] | 1.32e-07
[58 empty] | 9.2 | 0.0001-2.934422i | 0.000000001 | 0.010799+9.93478i | 5399336805.55556+0.0001i |  | 0.010799001+9.93478i | 58307443.561538+53641223309.0973i | 5399336805.56636+9.93488i | 0.010799+9.93478i | 0.010899+7.000358i | [12 empty] | 9.8 | 7.8279 | [16 empty] | 7.8e-08
[58 empty] | 9.4 | 0.0001-2.871988i | 0.000000001 | 0.010799+10.150753i | 5399336805.55556+0.0001i |  | 0.010799001+10.150753i | 58307443.561516+54807334277.0035i | 5399336805.56636+10.150853i | 0.010799+10.150753i | 0.010899+7.278765i | [12 empty] | 10 | 8.099 | [16 empty] | 6.8e-08
[58 empty] | 9.6 | 0.0001-2.812155i | 0.000000001 | 0.010799+10.366727i | 5399336805.55556+0.0001i |  | 0.010799001+10.366727i | 58307443.561495+55973450644.2466i | 5399336805.56636+10.366827i | 0.010799+10.366727i | 0.010899+7.554572i | [12 empty] | 10.2 | 8.3679 | [16 empty] | 3.8e-08
[58 empty] | 9.8 | 0.0001-2.754764i | 0.000000001 | 0.010799+10.5827i | 5399336805.55556+0.0001i |  | 0.010799001+10.5827i | 58307443.561473+57139561612.1528i | 5399336805.56636+10.5828i | 0.010799+10.5827i | 0.010899+7.827936i | [12 empty] | 10.4 | 8.6348 | [16 empty] | 4.6e-08
[58 empty] | 10 | 0.0001-2.699668i | 0.000000001 | 0.010799+10.798674i | 5399336805.55556+0.0001i |  | 0.010799001+10.798674i | 58307443.561451+58305677979.3959i | 5399336805.56636+10.798774i | 0.010799+10.798674i | 0.010899+8.099006i | [12 empty] | 10.6 | 8.8997 | [16 empty] | 5e-08
| Enter Customer PO # ¦ Stage 1 | [33 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 10.2 | 0.0001-2.646734i | 0.000000001 | 0.010799+11.014647i | 5399336805.55556+0.0001i |  | 0.010799001+11.014647i | 58307443.56143+59471788947.3021i | 5399336805.56636+11.014747i | 0.010799+11.014647i | 0.010899+8.367913i | [12 empty] | 10.8 | 9.1629 | [16 empty] | 0
[58 empty] | 10.4 | 0.0001-2.595835i | 0.000000001 | 0.010799+11.230621i | 5399336805.55556+0.0001i |  | 0.010799001+11.230621i | 58307443.561408+60637905314.5452i | 5399336805.56636+11.230721i | 0.010799+11.230621i | 0.010899+8.634786i | [12 empty] | 11 | 9.4243 | [16 empty] | 0
| Table of Currents and Voltages | [33 empty] | 📐 SIMPLIFIED ONE-LINE DIAGRAM | [18 empty] | (In) Filter Current | (In) Filter Current | Calculated Reactor Current | VarStec Reactor Rating | 10.6 | 0.0001-2.546857i | 0.000000001 | 0.010799+11.446594i | 5399336805.55556+0.0001i |  | 0.010799001+11.446594i | 58307443.561387+61804016282.4514i | 5399336805.56636+11.446694i | 0.010799+11.446594i | 0.010899+8.899737i | [12 empty] | 11.2 | 9.6841 | [16 empty] | 7e-08
[16 empty] | IREACTOR CURRENT (amps) | [41 empty] | 10.8 | 0.0001-2.499693i | 0.000000001 | 0.010799+11.662568i | 5399336805.55556+0.0001i |  | 0.010799001+11.662568i | 58307443.561365+62970132649.6945i | 5399336805.56636+11.662668i | 0.010799+11.662568i | 0.010899+9.162875i | [12 empty] | 11.4 | 9.9424 | [16 empty] | 7.4e-08
[6 empty] | (In) Filter Current (amps): |  |  |  |  | VCAP Voltage (volts) | [23 empty] | 12.47kV, 60Hz High-Pass Filter, Wye-Connected | [22 empty] | 11 | 0.0001-2.454244i | 0.000000001 | 0.010799+11.878541i | 5399336805.55556+0.0001i |  | 0.010799001+11.878541i | 58307443.561343+64136243617.6007i | 5399336805.56636+11.878641i | 0.010799+11.878541i | 0.010899+9.424297i | [12 empty] | 11.6 | 10.1992 | [16 empty] | 2.6496e-07
| Harmonic #: (n) | [19 empty] | Voltage Distortion* | [13 empty] | 6,000 Kvar 3-Phase, 5.0 Tuning | [22 empty] | 11.2 | 0.0001-2.410418i | 0.000000001 | 0.010799+12.094514i | 5399336805.55556+0.0001i |  | 0.010799001+12.094514i | 58307443.561322+65302354585.507i | 5399336805.56636+12.094614i | 0.010799+12.094514i | 0.010899+9.684096i | [12 empty] | 11.8 | 10.4546
[54 empty] | 1 | 278.1241 | 278.1241 | 417.1862 | 11.4 | 0.0001-2.36813i | 0.000000001 | 0.010799+12.310488i | 5399336805.55556+0.0001i |  | 0.010799001+12.310488i | 58307443.5613+66468470952.7501i | 5399336805.56636+12.310588i | 0.010799+12.310488i | 0.010899+9.942358i | [12 empty] | 12 | 10.7087 | [8 empty] | High-Pass Resistor Losses, 60 Hertz: | [5 empty] | 5.0119e-05 | Watts, 3-Phase or 0 BTUs/Hour
| 1 |  |  |  |  | 278.1241 |  |  |  |  | 7508.4297 |  |  |  |  | 278.1241 |  |  |  |  | 100.1% | [23 empty] | Fundamental amps 278.1 amps/phase | [8 empty] | 2 | 0 | 0 | 0 | 11.6 | 0.0001-2.3273i | 0.000000001 | 0.010799+12.526461i | 5399336805.55556+0.0001i |  | 0.010799001+12.526461i | 58307443.561279+67634581920.6563i | 5399336805.56636+12.526561i | 0.010799+12.526461i | 0.010899+10.199161i | [12 empty] | 12.2 | 10.9615
| 2 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0% | [23 empty] | RMS Current 314.89 amps/phase | [8 empty] | 3 | 0 | 0 | 0 | 11.8 | 0.0001-2.287855i | 0.000000001 | 0.010799+12.742435i | 5399336805.55556+0.0001i |  | 0.010799001+12.742435i | 58307443.561257+68800698287.8994i | 5399336805.56636+12.742535i | 0.010799+12.742435i | 0.010899+10.45458i | [12 empty] | 12.4 | 11.2132
| 3 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0% | [32 empty] | 4 | 0 | 0 | 0 | 12 | 0.0001-2.249724i | 0.000000001 | 0.010799+12.958408i | 5399336805.55556+0.0001i |  | 0.010799001+12.958408i | 58307443.561236+69966809255.8056i | 5399336805.56636+12.958508i | 0.010799+12.958408i | 0.010899+10.708684i | [12 empty] | 12.6 | 11.4637
| 4 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0% | [23 empty] | Reactor: 1.08 ohms, 2.86 mH | [8 empty] | 5 | 100 | 100 | 150 | 12.2 | 0.0001-2.212843i | 0.000000001 | 0.010799+13.174382i | 5399336805.55556+0.0001i |  | 0.010799001+13.174382i | 58307443.561214+71132925623.0487i | 5399336805.56636+13.174482i | 0.010799+13.174382i | 0.010899+10.961539i | [12 empty] | 12.8 | 11.7132
| 5 |  |  |  |  | 100 |  |  |  |  | 539.9337 |  |  |  |  | 100 |  |  |  |  | 0.01514% | [23 empty] | I1= 278.1 amps nominal | [8 empty] | 7 | 80 | 80 | 120 | 12.4 | 0.0001-2.177152i | 0.000000001 | 0.010799+13.390355i | 5399336805.55556+0.0001i |  | 0.010799001+13.390355i | 58307443.561192+72299036590.9549i | 5399336805.56636+13.390455i | 0.010799+13.390355i | 0.010899+11.213203i | [12 empty] | 13 | 11.9616
| 7 |  |  |  |  | 80 |  |  |  |  | 308.5335 |  |  |  |  | 80 |  |  |  |  | 4.114% | [32 empty] | 11 | 60 | 60 | 90 | 12.6 | 0.0001-2.142594i | 0.000000001 | 0.010799+13.606329i | 5399336805.55556+0.0001i |  | 0.010799001+13.606329i | 58307443.561171+73465152958.198i | 5399336805.56636+13.606429i | 0.010799+13.606329i | 0.010899+11.463735i | [12 empty] | 13.2 | 12.2091
| 11 |  |  |  |  | 60 |  |  |  |  | 147.2546 |  |  |  |  | 60 |  |  |  |  | 7.854% | [32 empty] | 13 | 30 | 30 | 45 | 12.8 | 0.0001-2.109116i | 0.000000001 | 0.010799+13.822302i | 5399336805.55556+0.0001i |  | 0.010799001+13.822302i | 58307443.561149+74631263926.1042i | 5399336805.56636+13.822402i | 0.010799+13.822302i | 0.010899+11.713186i | [12 empty] | 13.4 | 12.4555
| 13 |  |  |  |  | 30 |  |  |  |  | 62.3 |  |  |  |  | 30 |  |  |  |  | 4.984% | [32 empty] | 17 | 20 | 20 | 30 | 13 | 0.0001-2.076668i | 0.000000001 | 0.010799+14.038276i | 5399336805.55556+0.0001i |  | 0.010799001+14.038276i | 58307443.561128+75797380293.3473i | 5399336805.56636+14.038376i | 0.010799+14.038276i | 0.010899+11.961608i | [12 empty] | 13.6 | 12.7012
| 17 |  |  |  |  | 20 |  |  |  |  | 31.7608 |  |  |  |  | 20 |  |  |  |  | 4.659% | [32 empty] | 19 | 10 | 10 | 15 | 13.2 | 0.0001-2.045203i | 0.000000001 | 0.010799+14.254249i | 5399336805.55556+0.0001i |  | 0.010799001+14.254249i | 58307443.561106+76963491261.2535i | 5399336805.56636+14.254349i | 0.010799+14.254249i | 0.010899+12.209046i | [12 empty] | 13.8 | 12.9459
| 19 |  |  |  |  | 10 |  |  |  |  | 14.2088 |  |  |  |  | 10 |  |  |  |  | 2.652% | [23 empty] | Capacitor Fuse: 100 (Minimum Amps) | [8 empty] | 23 | 10 | 10 | 15 | 13.4 | 0.0001-2.014678i | 0.000000001 | 0.010799+14.470223i | 5399336805.55556+0.0001i |  | 0.010799001+14.470223i | 58307443.561084+78129607628.4966i | 5399336805.56636+14.470323i | 0.010799+14.470223i | 0.010899+12.455545i | [12 empty] | 14 | 13.1898
| 23 |  |  |  |  | 10 |  |  |  |  | 11.7377 |  |  |  |  | 10 |  |  |  |  | 3.287% | [32 empty] | 25 | 10 | 10 | 15 | 13.6 | 0.0001-1.98505i | 0.000000001 | 0.010799+14.686196i | 5399336805.55556+0.0001i |  | 0.010799001+14.686196i | 58307443.561063+79295718596.4028i | 5399336805.56636+14.686296i | 0.010799+14.686196i | 0.010899+12.701146i | [12 empty] | 14.2 | 13.4329
| 25 |  |  |  |  | 10 |  |  |  |  | 10.7987 |  |  |  |  | 10 |  |  |  |  | 3.6% | [32 empty] | 29 | 0 | 0 | 0 | 13.8 | 0.0001-1.956281i | 0.000000001 | 0.010799+14.90217i | 5399336805.55556+0.0001i |  | 0.010799001+14.90217i | 58307443.561041+80461834963.6459i | 5399336805.56636+14.90227i | 0.010799+14.90217i | 0.010899+12.945889i | [12 empty] | 14.4 | 13.6753
| 29 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0% | [23 empty] | Capacitor: Qty(15), 735 kvar, 9.96 kV, 19.65 µF/Can | [8 empty] | 31 | 0 | 0 | 0 | 14 | 0.0001-1.928335i | 0.000000001 | 0.010799+15.118143i | 5399336805.55556+0.0001i |  | 0.010799001+15.118143i | 58307443.56102+81627945931.5522i | 5399336805.56636+15.118243i | 0.010799+15.118143i | 0.010899+13.189808i | [12 empty] | 14.6 | 13.917
| 31 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0% | [32 empty] | 35 | 10 | 10 | 15 | 14.2 | 0.0001-1.901175i | 0.000000001 | 0.010799+15.334117i | 5399336805.55556+0.0001i |  | 0.010799001+15.334117i | 58307443.560998+82794062298.7952i | 5399336805.56636+15.334217i | 0.010799+15.334117i | 0.010899+13.432942i | [12 empty] | 14.8 | 14.1579
| 35 |  |  |  |  | 10 |  |  |  |  | 7.7133 |  |  |  |  | 10 |  |  |  |  | 5.143% | [32 empty] | 37 | 10 | 10 | 15 | 14.4 | 0.0001-1.87477i | 0.000000001 | 0.010799+15.55009i | 5399336805.55556+0.0001i |  | 0.010799001+15.55009i | 58307443.560976+83960173266.7015i | 5399336805.56636+15.55019i | 0.010799+15.55009i | 0.010899+13.67532i | [12 empty] | 15 | 14.3982
| 37 |  |  |  |  | 10 |  |  |  |  | 7.2964 |  |  |  |  | 10 |  |  |  |  | 5.448% | [36 empty] | 14.6 | 0.0001-1.849088i | 0.000000001 | 0.010799+15.766063i | 5399336805.55556+0.0001i |  | 0.010799001+15.766063i | 58307443.560955+85126284234.6077i | 5399336805.56636+15.766163i | 0.010799+15.766063i | 0.010899+13.916975i | [12 empty] | 15.2 | 14.6379
[5 empty] | RMS | 314.8858 |  |  |  |  | 7535.9885 |  |  |  |  | 314.8858 |  |  |  |  | 14.56% | [36 empty] | 14.8 | 0.0001-1.8241i | 0.000000001 | 0.010799+15.982037i | 5399336805.55556+0.0001i |  | 0.010799001+15.982037i | 58307443.560933+86292400601.8508i | 5399336805.56636+15.982137i | 0.010799+15.982037i | 0.010899+14.157937i | [12 empty] | 15.4 | 14.8769
| * Voltage distortion at filter incoming based on specified harmonic currents in rows 24 and 25 of page 1. | [56 empty] | 15 | 0.0001-1.799779i | 0.000000001 | 0.010799+16.19801i | 5399336805.55556+0.0001i |  | 0.010799001+16.19801i | 58307443.560912+87458511569.757i | 5399336805.56636+16.19811i | 0.010799+16.19801i | 0.010899+14.398231i | [12 empty] | 15.6 | 15.1154
[58 empty] | 15.2 | 0.0001-1.776098i | 0.000000001 | 0.010799+16.413984i | 5399336805.55556+0.0001i |  | 0.010799001+16.413984i | 58307443.56089+88624627937.0001i | 5399336805.56636+16.414084i | 0.010799+16.413984i | 0.010899+14.637886i | [12 empty] | 15.8 | 15.3533
[58 empty] | 15.4 | 0.0001-1.753031i | 0.000000001 | 0.010799+16.629957i | 5399336805.55556+0.0001i |  | 0.010799001+16.629957i | 58307443.560868+89790738904.9063i | 5399336805.56636+16.630057i | 0.010799+16.629957i | 0.010899+14.876926i | [12 empty] | 16 | 15.5906
[58 empty] | 15.6 | 0.0001-1.730557i | 0.000000001 | 0.010799+16.845931i | 5399336805.55556+0.0001i |  | 0.010799001+16.845931i | 58307443.560847+90956855272.1494i | 5399336805.56636+16.846031i | 0.010799+16.845931i | 0.010899+15.115374i | [12 empty] | 16.2 | 15.8274
[58 empty] | 15.8 | 0.0001-1.708651i | 0.000000001 | 0.010799+17.061904i | 5399336805.55556+0.0001i |  | 0.010799001+17.061904i | 58307443.560825+92122966240.0556i | 5399336805.56636+17.062004i | 0.010799+17.061904i | 0.010899+15.353253i | [12 empty] | 16.4 | 16.0637
[58 empty] | 16 | 0.0001-1.687293i | 0.000000001 | 0.010799+17.277878i | 5399336805.55556+0.0001i |  | 0.010799001+17.277878i | 58307443.560804+93289082607.2987i | 5399336805.56636+17.277978i | 0.010799+17.277878i | 0.010899+15.590585i | [12 empty] | 16.6 | 16.2995
[58 empty] | 16.2 | 0.0001-1.666462i | 0.000000001 | 0.010799+17.493851i | 5399336805.55556+0.0001i |  | 0.010799001+17.493851i | 58307443.560782+94455193575.2049i | 5399336805.56636+17.493951i | 0.010799+17.493851i | 0.010899+15.827389i | [12 empty] | 16.8 | 16.5348
[58 empty] | 16.4 | 0.0001-1.646139i | 0.000000001 | 0.010799+17.709825i | 5399336805.55556+0.0001i |  | 0.010799001+17.709825i | 58307443.56076+95621309942.448i | 5399336805.56636+17.709925i | 0.010799+17.709825i | 0.010899+16.063686i | [12 empty] | 17 | 16.7697
[58 empty] | 16.6 | 0.0001-1.626306i | 0.000000001 | 0.010799+17.925798i | 5399336805.55556+0.0001i |  | 0.010799001+17.925798i | 58307443.560739+96787420910.3542i | 5399336805.56636+17.925898i | 0.010799+17.925798i | 0.010899+16.299492i | [12 empty] | 17.2 | 17.0041
[58 empty] | 16.8 | 0.0001-1.606945i | 0.000000001 | 0.010799+18.141772i | 5399336805.55556+0.0001i |  | 0.010799001+18.141772i | 58307443.560717+97953537277.5973i | 5399336805.56636+18.141872i | 0.010799+18.141772i | 0.010899+16.534827i | [12 empty] | 17.4 | 17.2382
[58 empty] | 17 | 0.0001-1.58804i | 0.000000001 | 0.010799+18.357745i | 5399336805.55556+0.0001i |  | 0.010799001+18.357745i | 58307443.560696+99119648245.5036i | 5399336805.56636+18.357845i | 0.010799+18.357745i | 0.010899+16.769705i | [12 empty] | 17.6 | 17.4718
[58 empty] | 17.2 | 0.0001-1.569575i | 0.000000001 | 0.010799+18.573719i | 5399336805.55556+0.0001i |  | 0.010799001+18.573719i | 58307443.560674+100285764612.747i | 5399336805.56636+18.573819i | 0.010799+18.573719i | 0.010899+17.004144i | [12 empty] | 17.8 | 17.705
[58 empty] | 17.4 | 0.0001-1.551534i | 0.000000001 | 0.010799+18.789692i | 5399336805.55556+0.0001i |  | 0.010799001+18.789692i | 58307443.560652+101451875580.653i | 5399336805.56636+18.789792i | 0.010799+18.789692i | 0.010899+17.238158i | [12 empty] | 18 | 17.9378
[58 empty] | 17.6 | 0.0001-1.533903i | 0.000000001 | 0.010799+19.005666i | 5399336805.55556+0.0001i |  | 0.010799001+19.005666i | 58307443.560631+102617991947.896i | 5399336805.56636+19.005766i | 0.010799+19.005666i | 0.010899+17.471763i | [12 empty] | 18.2 | 18.1703
[58 empty] | 17.8 | 0.0001-1.516668i | 0.000000001 | 0.010799+19.221639i | 5399336805.55556+0.0001i |  | 0.010799001+19.221639i | 58307443.560609+103784102915.802i | 5399336805.56636+19.221739i | 0.010799+19.221639i | 0.010899+17.704971i | [12 empty] | 18.4 | 18.4024
[58 empty] | 18 | 0.0001-1.499816i | 0.000000001 | 0.010799+19.437613i | 5399336805.55556+0.0001i |  | 0.010799001+19.437613i | 58307443.560588+104950219283.045i | 5399336805.56636+19.437713i | 0.010799+19.437613i | 0.010899+17.937797i | [12 empty] | 18.6 | 18.6341
[58 empty] | 18.2 | 0.0001-1.483334i | 0.000000001 | 0.010799+19.653586i | 5399336805.55556+0.0001i |  | 0.010799001+19.653586i | 58307443.560566+106116330250.951i | 5399336805.56636+19.653686i | 0.010799+19.653586i | 0.010899+18.170252i | [12 empty] | 18.8 | 18.8655
[58 empty] | 18.4 | 0.0001-1.467211i | 0.000000001 | 0.010799+19.869559i | 5399336805.55556+0.0001i |  | 0.010799001+19.869559i | 58307443.560544+107282441218.858i | 5399336805.56636+19.869659i | 0.010799+19.869559i | 0.010899+18.402348i | [12 empty] | 19 | 19.0966
[58 empty] | 18.6 | 0.0001-1.451435i | 0.000000001 | 0.010799+20.085533i | 5399336805.55556+0.0001i |  | 0.010799001+20.085533i | 58307443.560523+108448557586.101i | 5399336805.56636+20.085633i | 0.010799+20.085533i | 0.010899+18.634098i | [12 empty] | 19.2 | 19.3274
|  | Info@VarStec.com | [31 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 4 ¦ P a g e |  |  |  |  | 18.8 | 0.0001-1.435994i | 0.000000001 | 0.010799+20.301506i | 5399336805.55556+0.0001i |  | 0.010799001+20.301506i | 58307443.560501+109614668554.007i | 5399336805.56636+20.301606i | 0.010799+20.301506i | 0.010899+18.865512i | [12 empty] | 19.4 | 19.5578
[58 empty] | 19 | 0.0001-1.420878i | 0.000000001 | 0.010799+20.51748i | 5399336805.55556+0.0001i |  | 0.010799001+20.51748i | 58307443.56048+110780784921.25i | 5399336805.56636+20.51758i | 0.010799+20.51748i | 0.010899+19.096602i | [12 empty] | 19.6 | 19.788
[58 empty] | 19.2 | 0.0001-1.406077i | 0.000000001 | 0.010799+20.733453i | 5399336805.55556+0.0001i |  | 0.010799001+20.733453i | 58307443.560458+111946895889.156i | 5399336805.56636+20.733553i | 0.010799+20.733453i | 0.010899+19.327376i | [12 empty] | 19.8 | 20.0179
[58 empty] | 19.4 | 0.0001-1.391582i | 0.000000001 | 0.010799+20.949427i | 5399336805.55556+0.0001i |  | 0.010799001+20.949427i | 58307443.560436+113113012256.399i | 5399336805.56636+20.949527i | 0.010799+20.949427i | 0.010899+19.557845i | [12 empty] | 20 | 20.2475
[58 empty] | 19.6 | 0.0001-1.377382i | 0.000000001 | 0.010799+21.1654i | 5399336805.55556+0.0001i |  | 0.010799001+21.1654i | 58307443.560415+114279123224.306i | 5399336805.56636+21.1655i | 0.010799+21.1654i | 0.010899+19.788018i | [12 empty] | 20.2 | 20.4769
[58 empty] | 19.8 | 0.0001-1.363469i | 0.000000001 | 0.010799+21.381374i | 5399336805.55556+0.0001i |  | 0.010799001+21.381374i | 58307443.560393+115445239591.549i | 5399336805.56636+21.381474i | 0.010799+21.381374i | 0.010899+20.017905i | [12 empty] | 20.4 | 20.7059
| Enter Customer PO # ¦ Stage 1 | [33 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 20 | 0.0001-1.349834i | 0.000000001 | 0.010799+21.597347i | 5399336805.55556+0.0001i |  | 0.010799001+21.597347i | 58307443.560372+116611350559.455i | 5399336805.56636+21.597447i | 0.010799+21.597347i | 0.010899+20.247513i | [12 empty] | 20.6 | 20.9348
[58 empty] | 20.2 | 0.0001-1.33647i | 0.000000001 | 0.010799+21.813321i | 5399336805.55556+0.0001i |  | 0.010799001+21.813321i | 58307443.56035+117777466926.698i | 5399336805.56636+21.813421i | 0.010799+21.813321i | 0.010899+20.476851i | [12 empty] | 20.8 | 21.1633
| 🧮 VENDOR SPECIFICATIONS | [33 empty] | 🧮 3-PHASE LOSS ESTIMATES | [22 empty] | 20.4 | 0.0001-1.323367i | 0.000000001 | 0.010799+22.029294i | 5399336805.55556+0.0001i |  | 0.010799001+22.029294i | 58307443.560328+118943577894.604i | 5399336805.56636+22.029394i | 0.010799+22.029294i | 0.010899+20.705927i | [12 empty] | 21 | 21.3917
|  | Reactor Specification | [55 empty] | 20.6 | 0.0001-1.310519i | 0.000000001 | 0.010799+22.245268i | 5399336805.55556+0.0001i |  | 0.010799001+22.245268i | 58307443.560307+120109694261.847i | 5399336805.56636+22.245368i | 0.010799+22.245268i | 0.010899+20.934749i | [12 empty] | 21.2 | 21.6198
[35 empty] | 60 Hertz Losses | [22 empty] | 20.8 | 0.0001-1.297918i | 0.000000001 | 0.010799+22.461241i | 5399336805.55556+0.0001i |  | 0.010799001+22.461241i | 58307443.560285+121275805229.754i | 5399336805.56636+22.461341i | 0.010799+22.461241i | 0.010899+21.163323i | [12 empty] | 21.4 | 21.8476
|  |  |  | Filter Type: | Notch Tuned | [12 empty] | Return Quote to: | VarStec Power Solutions | [16 empty] | Capacitor Losses: | [6 empty] | 1102.3754 |  |  | Watts, 3-Phase or 3761 BTUs/Hour | [11 empty] | 21 | 0.0001-1.285556i | 0.000000001 | 0.010799+22.677215i | 5399336805.55556+0.0001i |  | 0.010799001+22.677215i | 58307443.560264+122441921596.997i | 5399336805.56636+22.677315i | 0.010799+22.677215i | 0.010899+21.391659i | [12 empty] | 21.6 | 22.0753
|  |  |  | Stage/Branch: | Stage 1 | [30 empty] | Capacitor Fuse Losses: | [6 empty] | 3033.5537 |  |  | Watts, 3-Phase or 10351 BTUs/Hour | [11 empty] | 21.2 | 0.0001-1.273428i | 0.000000001 | 0.010799+22.893188i | 5399336805.55556+0.0001i |  | 0.010799001+22.893188i | 58307443.560242+123608032564.903i | 5399336805.56636+22.893288i | 0.010799+22.893188i | 0.010899+21.61976i | [12 empty] | 21.8 | 22.3027
|  |  |  | Tuning Point: | 5 | [30 empty] | Iron-Core Reactor Losses, 60 Hertz: | [6 empty] | 2505.9307 |  |  | Watts, 3-Phase or 8551 BTUs/Hour | [11 empty] | 21.4 | 0.0001-1.261527i | 0.000000001 | 0.010799+23.109162i | 5399336805.55556+0.0001i |  | 0.010799001+23.109162i | 58307443.56022+124774148932.146i | 5399336805.56636+23.109262i | 0.010799+23.109162i | 0.010899+21.847635i | [12 empty] | 22 | 22.53
[36 empty] | Total 60 Hz Losses: | [6 empty] | 6641.8598 |  |  | Watts, 3-Phase or 22663 BTUs/Hour | [11 empty] | 21.6 | 0.0001-1.249846i | 0.000000001 | 0.010799+23.325135i | 5399336805.55556+0.0001i |  | 0.010799001+23.325135i | 58307443.560199+125940259900.052i | 5399336805.56636+23.325235i | 0.010799+23.325135i | 0.010899+22.075289i | [12 empty] | 22.2 | 22.757
|  | Current Spectrum | [6 empty] | Tuning Reactor Details | [48 empty] | 21.8 | 0.0001-1.23838i | 0.000000001 | 0.010799+23.541108i | 5399336805.55556+0.0001i |  | 0.010799001+23.541108i | 58307443.560177+127106370867.958i | 5399336805.56636+23.541208i | 0.010799+23.541108i | 0.010899+22.302728i | [12 empty] | 22.4 | 22.9838
|  | Harm # |  |  | Amps | [11 empty] | Quantity: | 3 | [39 empty] | 22 | 0.0001-1.227122i | 0.000000001 | 0.010799+23.757082i | 5399336805.55556+0.0001i |  | 0.010799001+23.757082i | 58307443.560156+128272487235.201i | 5399336805.56636+23.757182i | 0.010799+23.757082i | 0.010899+22.52996i | [12 empty] | 22.6 | 23.2105
|  | 1 |  |  | 417.1862 | [11 empty] | Number of Phases: | 1 | [17 empty] | Harmonic Losses Based on Specified Harmonics | [21 empty] | 22.2 | 0.0001-1.216067i | 0.000000001 | 0.010799+23.973055i | 5399336805.55556+0.0001i |  | 0.010799001+23.973055i | 58307443.560134+129438598203.108i | 5399336805.56636+23.973155i | 0.010799+23.973055i | 0.010899+22.756988i | [12 empty] | 22.8 | 23.4369
|  | 2 |  |  | 0 | [11 empty] | System Voltage: | 12.47 |  | kV | [21 empty] | Iron-Core Reactor Losses: | 706.2333 |  |  |  | Watts, 3-Phase or 2410 BTUs/Hour | [10 empty] | 22.4 | 0.0001-1.205209i | 0.000000001 | 0.010799+24.189029i | 5399336805.55556+0.0001i |  | 0.010799001+24.189029i | 58307443.560112+130604714570.351i | 5399336805.56636+24.189129i | 0.010799+24.189029i | 0.010899+22.98382i | [12 empty] | 23 | 23.6632
|  | 3 |  |  | 0 | [11 empty] | BIL Rating: | 95 |  | kV | [21 empty] | Total Harmonic Losses: | 706.2333 |  |  |  | Watts, 3-Phase or 2410 BTUs/Hour | [10 empty] | 22.6 | 0.0001-1.194544i | 0.000000001 | 0.010799+24.405002i | 5399336805.55556+0.0001i |  | 0.010799001+24.405002i | 58307443.560091+131770825538.257i | 5399336805.56636+24.405102i | 0.010799+24.405002i | 0.010899+23.210458i | [12 empty] | 23.2 | 23.8893
|  | 4 |  |  | 0 | [11 empty] | 60 Second Withstand Voltage: | 35 |  | kV | [37 empty] | 22.8 | 0.0001-1.184065i | 0.000000001 | 0.010799+24.620976i | 5399336805.55556+0.0001i |  | 0.010799001+24.620976i | 58307443.560069+132936941905.5i | 5399336805.56636+24.621076i | 0.010799+24.620976i | 0.010899+23.436911i | [12 empty] | 23.4 | 24.1152
|  | 5 |  |  | 150 | [11 empty] | Fundamental Frequency: | 60 |  | Hz | [21 empty] | Total Losses - All: | 7348.0931 |  |  |  | Watts, 3-Phase or 25073 BTUs/Hour | [10 empty] | 23 | 0.0001-1.173769i | 0.000000001 | 0.010799+24.836949i | 5399336805.55556+0.0001i |  | 0.010799001+24.836949i | 58307443.560048+134103052873.406i | 5399336805.56636+24.837049i | 0.010799+24.836949i | 0.010899+23.66318i | [12 empty] | 23.6 | 24.3409
|  | 7 |  |  | 120 | [11 empty] | Inductance: | 2.8645 |  | mH | [37 empty] | 23.2 | 0.0001-1.16365i | 0.000000001 | 0.010799+25.052923i | 5399336805.55556+0.0001i |  | 0.010799001+25.052923i | 58307443.560026+135269169240.649i | 5399336805.56636+25.053023i | 0.010799+25.052923i | 0.010899+23.889273i | [12 empty] | 23.8 | 24.5665
|  | 11 |  |  | 90 | [11 empty] | Reactance at 60Hz: | 1.0799 |  | Ohms | [37 empty] | 23.4 | 0.0001-1.153704i | 0.000000001 | 0.010799+25.268896i | 5399336805.55556+0.0001i |  | 0.010799001+25.268896i | 58307443.560004+136435280208.556i | 5399336805.56636+25.268996i | 0.010799+25.268896i | 0.010899+24.115192i | [12 empty] | 24 | 24.792
|  | 13 |  |  | 45 | [11 empty] | Taps: | None | [39 empty] | 23.6 | 0.0001-1.143927i | 0.000000001 | 0.010799+25.48487i | 5399336805.55556+0.0001i |  | 0.010799001+25.48487i | 58307443.559983+137601396575.799i | 5399336805.56636+25.48497i | 0.010799+25.48487i | 0.010899+24.340943i | [12 empty] | 24.2 | 25.0172
|  | 17 |  |  | 30 | [11 empty] | Insulation Type: | Nomex | [39 empty] | 23.8 | 0.0001-1.134314i | 0.000000001 | 0.010799+25.700843i | 5399336805.55556+0.0001i |  | 0.010799001+25.700843i | 58307443.559961+138767507543.705i | 5399336805.56636+25.700943i | 0.010799+25.700843i | 0.010899+24.566529i | [12 empty] | 24.4 | 25.2423
|  | 19 |  |  | 15 | [11 empty] | Ambient: | 60C | [16 empty] | 🧮 HARMONIC FILTER DESIGN METHODOLOGY | [22 empty] | 24 | 0.0001-1.124862i | 0.000000001 | 0.010799+25.916817i | 5399336805.55556+0.0001i |  | 0.010799001+25.916817i | 58307443.55994+139933623910.948i | 5399336805.56636+25.916917i | 0.010799+25.916817i | 0.010899+24.791955i | [12 empty] | 24.6 | 25.4673
|  | 23 |  |  | 15 | [11 empty] | Temperature Rise: | 115C Rise over Ambient | [39 empty] | 24.2 | 0.0001-1.115565i | 0.000000001 | 0.010799+26.13279i | 5399336805.55556+0.0001i |  | 0.010799001+26.13279i | 58307443.559918+141099734878.854i | 5399336805.56636+26.13289i | 0.010799+26.13279i | 0.010899+25.017225i | [12 empty] | 24.8 | 25.6921
|  | 25 |  |  | 15 | [11 empty] | Winding Type: | CU/AL - Based On Price | [39 empty] | 24.4 | 0.0001-1.106421i | 0.000000001 | 0.010799+26.348764i | 5399336805.55556+0.0001i |  | 0.010799001+26.348764i | 58307443.559896+142265851246.097i | 5399336805.56636+26.348864i | 0.010799+26.348764i | 0.010899+25.242343i | [12 empty] | 25 | 25.9168
|  | 29 |  |  | 0 | [11 empty] | Tack Winding to Core: | Yes | [39 empty] | 24.6 | 0.0001-1.097426i | 0.000000001 | 0.010799+26.564737i | 5399336805.55556+0.0001i |  | 0.010799001+26.564737i | 58307443.559875+143431962214.004i | 5399336805.56636+26.564837i | 0.010799+26.564737i | 0.010899+25.467311i | [12 empty] | 25.2 | 26.1414
|  | 31 |  |  | 0 | [11 empty] | Enclosure: | None/Open Construction | [39 empty] | 24.8 | 0.0001-1.088576i | 0.000000001 | 0.010799+26.780711i | 5399336805.55556+0.0001i |  | 0.010799001+26.780711i | 58307443.559853+144598078581.247i | 5399336805.56636+26.780811i | 0.010799+26.780711i | 0.010899+25.692135i | [12 empty] | 25.4 | 26.3658
|  | 35 |  |  | 15 | [52 empty] | 25 | 0.0001-1.079867i | 0.000000001 | 0.010799+26.996684i | 5399336805.55556+0.0001i |  | 0.010799001+26.996684i | 58307443.559832+145764189549.153i | 5399336805.56636+26.996784i | 0.010799+26.996684i | 0.010899+25.916817i | [12 empty] | 25.6 | 26.59
|  | 37 |  |  | 15 | [52 empty] | 25.2 | 0.0001-1.071297i | 0.000000001 | 0.010799+27.212658i | 5399336805.55556+0.0001i |  | 0.010799001+27.212658i | 58307443.55981+146930305916.396i | 5399336805.56636+27.212758i | 0.010799+27.212658i | 0.010899+26.141361i | [12 empty] | 25.8 | 26.8142
|  | RMS: |  |  | 472.3286 | [52 empty] | 25.4 | 0.0001-1.062862i | 0.000000001 | 0.010799+27.428631i | 5399336805.55556+0.0001i |  | 0.010799001+27.428631i | 58307443.559788+148096416884.302i | 5399336805.56636+27.428731i | 0.010799+27.428631i | 0.010899+26.365769i | [12 empty] | 26 | 27.0382
| Capacitor Specification | [56 empty] | 25.6 | 0.0001-1.054558i | 0.000000001 | 0.010799+27.644604i | 5399336805.55556+0.0001i |  | 0.010799001+27.644604i | 58307443.559767+149262527852.208i | 5399336805.56636+27.644704i | 0.010799+27.644604i | 0.010899+26.590046i | [12 empty] | 26.2 | 27.2621
| A quantity of 15, 735 kvar, 95 kV BIL, 60 Hertz, all-film, low-loss, double-bushing capacitors designed, manufactured, and tested to applicable IEEE/ANSI and IEC standards, supplied by Cooper, GE, or Hitachi (no others), are required. The capacitors shall be connected unground-wye and shall have applicable over-voltage and blown-fuse protection. | [56 empty] | 25.8 | 0.0001-1.046383i | 0.000000001 | 0.010799+27.860578i | 5399336805.55556+0.0001i |  | 0.010799001+27.860578i | 58307443.559745+150428644219.452i | 5399336805.56636+27.860678i | 0.010799+27.860578i | 0.010899+26.814195i | [12 empty] | 26.4 | 27.4859
[58 empty] | 26 | 0.0001-1.038334i | 0.000000001 | 0.010799+28.076551i | 5399336805.55556+0.0001i |  | 0.010799001+28.076551i | 58307443.559724+151594755187.358i | 5399336805.56636+28.076651i | 0.010799+28.076551i | 0.010899+27.038217i | [12 empty] | 26.6 | 27.7096
[58 empty] | 26.2 | 0.0001-1.030408i | 0.000000001 | 0.010799+28.292525i | 5399336805.55556+0.0001i |  | 0.010799001+28.292525i | 58307443.559702+152760871554.601i | 5399336805.56636+28.292625i | 0.010799+28.292525i | 0.010899+27.262117i | [12 empty] | 26.8 | 27.9331
[58 empty] | 26.4 | 0.0001-1.022602i | 0.000000001 | 0.010799+28.508498i | 5399336805.55556+0.0001i |  | 0.010799001+28.508498i | 58307443.55968+153926982522.507i | 5399336805.56636+28.508598i | 0.010799+28.508498i | 0.010899+27.485896i | [12 empty] | 27 | 28.1565
| Notch ¦ High-Pass ¦ C-High-Pass Filter Design Considerations | [56 empty] | 26.6 | 0.0001-1.014913i | 0.000000001 | 0.010799+28.724472i | 5399336805.55556+0.0001i |  | 0.010799001+28.724472i | 58307443.559659+155093098889.75i | 5399336805.56636+28.724572i | 0.010799+28.724472i | 0.010899+27.709559i | [12 empty] | 27.2 | 28.3799
| The notch type harmonic filter is the most economical design and provides harmonic filtering, power factor correction, and suppression of resonance above its tuning point (providing there are no other capacitors on the system). It precludes resonances at its tuning frequency and also filters at its tuning frequency and at frequencies above (to a lesser degree as you get further from the tuning point). It does not include a damping resistor. Because of cost and complexity, only consider High Pass or C High Pass filter when interharmonic producing loads are present, on systems with significant stray capacitance (renewable power plants or large industrial systems), and on systems where a damped filter is being employed with a shunt power capacitor bank to reduce cost. | [56 empty] | 26.8 | 0.0001-1.007339i | 0.000000001 | 0.010799+28.940445i | 5399336805.55556+0.0001i |  | 0.010799001+28.940445i | 58307443.559637+156259209857.656i | 5399336805.56636+28.940545i | 0.010799+28.940445i | 0.010899+27.933106i | [12 empty] | 27.4 | 28.6031
[58 empty] | 27 | 0.0001-0.999877i | 0.000000001 | 0.010799+29.156419i | 5399336805.55556+0.0001i |  | 0.010799001+29.156419i | 58307443.559616+157425326224.899i | 5399336805.56636+29.156519i | 0.010799+29.156419i | 0.010899+28.156542i | [12 empty] | 27.6 | 28.8262
[58 empty] | 27.2 | 0.0001-0.992525i | 0.000000001 | 0.010799+29.372392i | 5399336805.55556+0.0001i |  | 0.010799001+29.372392i | 58307443.559594+158591437192.806i | 5399336805.56636+29.372492i | 0.010799+29.372392i | 0.010899+28.379867i | [12 empty] | 27.8 | 29.0492
[58 empty] | 27.4 | 0.0001-0.98528i | 0.000000001 | 0.010799+29.588366i | 5399336805.55556+0.0001i |  | 0.010799001+29.588366i | 58307443.559573+159757553560.049i | 5399336805.56636+29.588466i | 0.010799+29.588366i | 0.010899+28.603086i | [12 empty] | 28 | 29.2721
[58 empty] | 27.6 | 0.0001-0.978141i | 0.000000001 | 0.010799+29.804339i | 5399336805.55556+0.0001i |  | 0.010799001+29.804339i | 58307443.559551+160923664527.955i | 5399336805.56636+29.804439i | 0.010799+29.804339i | 0.010899+28.826198i | [12 empty] | 28.2 | 29.4949
[58 empty] | 27.8 | 0.0001-0.971104i | 0.000000001 | 0.010799+30.020313i | 5399336805.55556+0.0001i |  | 0.010799001+30.020313i | 58307443.559529+162089780895.198i | 5399336805.56636+30.020413i | 0.010799+30.020313i | 0.010899+29.049209i | [12 empty] | 28.4 | 29.7176
[58 empty] | 28 | 0.0001-0.964167i | 0.000000001 | 0.010799+30.236286i | 5399336805.55556+0.0001i |  | 0.010799001+30.236286i | 58307443.559508+163255891863.104i | 5399336805.56636+30.236386i | 0.010799+30.236286i | 0.010899+29.272119i | [12 empty] | 28.6 | 29.9403
[58 empty] | 28.2 | 0.0001-0.957329i | 0.000000001 | 0.010799+30.45226i | 5399336805.55556+0.0001i |  | 0.010799001+30.45226i | 58307443.559486+164422008230.347i | 5399336805.56636+30.45236i | 0.010799+30.45226i | 0.010899+29.494931i | [12 empty] | 28.8 | 30.1628
[58 empty] | 28.4 | 0.0001-0.950587i | 0.000000001 | 0.010799+30.668233i | 5399336805.55556+0.0001i |  | 0.010799001+30.668233i | 58307443.559465+165588119198.254i | 5399336805.56636+30.668333i | 0.010799+30.668233i | 0.010899+29.717646i | [12 empty] | 29 | 30.3852
|  | Info@VarStec.com | [31 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 6 ¦ P a g e |  |  |  |  | 28.6 | 0.0001-0.94394i | 0.000000001 | 0.010799+30.884207i | 5399336805.55556+0.0001i |  | 0.010799001+30.884207i | 58307443.559443+166754235565.497i | 5399336805.56636+30.884307i | 0.010799+30.884207i | 0.010899+29.940267i | [12 empty] | 29.2 | 30.6076
[58 empty] | 28.8 | 0.0001-0.937385i | 0.000000001 | 0.010799+31.10018i | 5399336805.55556+0.0001i |  | 0.010799001+31.10018i | 58307443.559421+167920346533.403i | 5399336805.56636+31.10028i | 0.010799+31.10018i | 0.010899+30.162795i | [12 empty] | 29.4 | 30.8298
[58 empty] | 29 | 0.0001-0.93092i | 0.000000001 | 0.010799+31.316153i | 5399336805.55556+0.0001i |  | 0.010799001+31.316153i | 58307443.5594+169086457501.309i | 5399336805.56636+31.316253i | 0.010799+31.316153i | 0.010899+30.385233i | [12 empty] | 29.6 | 31.052
[58 empty] | 29.2 | 0.0001-0.924544i | 0.000000001 | 0.010799+31.532127i | 5399336805.55556+0.0001i |  | 0.010799001+31.532127i | 58307443.559378+170252573868.552i | 5399336805.56636+31.532227i | 0.010799+31.532127i | 0.010899+30.607583i | [12 empty] | 29.8 | 31.2741
[58 empty] | 29.4 | 0.0001-0.918255i | 0.000000001 | 0.010799+31.7481i | 5399336805.55556+0.0001i |  | 0.010799001+31.7481i | 58307443.559357+171418684836.458i | 5399336805.56636+31.7482i | 0.010799+31.7481i | 0.010899+30.829845i | [12 empty] | 30 | 31.4961
[58 empty] | 29.6 | 0.0001-0.91205i | 0.000000001 | 0.010799+31.964074i | 5399336805.55556+0.0001i |  | 0.010799001+31.964074i | 58307443.559335+172584801203.702i | 5399336805.56636+31.964174i | 0.010799+31.964074i | 0.010899+31.052024i | [12 empty] | 30.2 | 31.7181
| Enter Customer PO # ¦ Stage 1 | [33 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 29.8 | 0.0001-0.905929i | 0.000000001 | 0.010799+32.180047i | 5399336805.55556+0.0001i |  | 0.010799001+32.180047i | 58307443.559313+173750912171.608i | 5399336805.56636+32.180147i | 0.010799+32.180047i | 0.010899+31.274118i | [12 empty] | 30.4 | 31.9399
[58 empty] | 30 | 0.0001-0.899889i | 0.000000001 | 0.010799+32.396021i | 5399336805.55556+0.0001i |  | 0.010799001+32.396021i | 58307443.559292+174917028538.851i | 5399336805.56636+32.396121i | 0.010799+32.396021i | 0.010899+31.496132i | [12 empty] | 30.6 | 32.1617
[35 empty] | Nomenclature and Parameter Definitions for Harmonic Filter Design | [22 empty] | 30.2 | 0.0001-0.89393i | 0.000000001 | 0.010799+32.611994i | 5399336805.55556+0.0001i |  | 0.010799001+32.611994i | 58307443.55927+176083139506.757i | 5399336805.56636+32.612094i | 0.010799+32.611994i | 0.010899+31.718064i | [12 empty] | 30.8 | 32.3834
[37 empty] | Xeff: |  | Effective reactance of the harmonic filter | [18 empty] | 30.4 | 0.0001-0.888049i | 0.000000001 | 0.010799+32.827968i | 5399336805.55556+0.0001i |  | 0.010799001+32.827968i | 58307443.559249+177249255874i | 5399336805.56636+32.828068i | 0.010799+32.827968i | 0.010899+31.939919i | [12 empty] | 31 | 32.605
[37 empty] | Qeff: |  | Effective reactive power output of the harmonic filter (considering fundamental current only) | [18 empty] | 30.6 | 0.0001-0.882245i | 0.000000001 | 0.010799+33.043941i | 5399336805.55556+0.0001i |  | 0.010799001+33.043941i | 58307443.559227+178415366841.906i | 5399336805.56636+33.044041i | 0.010799+33.043941i | 0.010899+32.161696i | [12 empty] | 31.2 | 32.8266
[37 empty] | QRATED PER PHASE: |  | kvar rating of main capacitor group at their rated voltage (not the application voltage) | [18 empty] | 30.8 | 0.0001-0.876516i | 0.000000001 | 0.010799+33.259915i | 5399336805.55556+0.0001i |  | 0.010799001+33.259915i | 58307443.559205+179581483209.149i | 5399336805.56636+33.260015i | 0.010799+33.259915i | 0.010899+32.383399i | [12 empty] | 31.4 | 33.0481
[37 empty] | VLLSYS: |  | Nominal system line-to-line voltage | [18 empty] | 31 | 0.0001-0.870861i | 0.000000001 | 0.010799+33.475888i | 5399336805.55556+0.0001i |  | 0.010799001+33.475888i | 58307443.559184+180747594177.056i | 5399336805.56636+33.475988i | 0.010799+33.475888i | 0.010899+32.605027i | [12 empty] | 31.6 | 33.2695
[37 empty] | XC: |  | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [18 empty] | 31.2 | 0.0001-0.865278i | 0.000000001 | 0.010799+33.691862i | 5399336805.55556+0.0001i |  | 0.010799001+33.691862i | 58307443.559162+181913710544.299i | 5399336805.56636+33.691962i | 0.010799+33.691862i | 0.010899+32.826584i | [12 empty] | 31.8 | 33.4908
[37 empty] | XL: |  | Inductive reactance of the harmonic filter reactor at fundamental frequency | [18 empty] | 31.4 | 0.0001-0.859767i | 0.000000001 | 0.010799+33.907835i | 5399336805.55556+0.0001i |  | 0.010799001+33.907835i | 58307443.559141+183079821512.205i | 5399336805.56636+33.907935i | 0.010799+33.907835i | 0.010899+33.048068i | [12 empty] | 32 | 33.7121
[37 empty] | hn: |  | harmonic number of filter tuning point | [18 empty] | 31.6 | 0.0001-0.854325i | 0.000000001 | 0.010799+34.123809i | 5399336805.55556+0.0001i |  | 0.010799001+34.123809i | 58307443.559119+184245937879.448i | 5399336805.56636+34.123909i | 0.010799+34.123809i | 0.010899+33.269484i | [12 empty] | 32.2 | 33.9333
[37 empty] | hf: |  | harmonic frequency of filter tuning point in Hertz | [18 empty] | 31.8 | 0.0001-0.848952i | 0.000000001 | 0.010799+34.339782i | 5399336805.55556+0.0001i |  | 0.010799001+34.339782i | 58307443.559097+185412048847.354i | 5399336805.56636+34.339882i | 0.010799+34.339782i | 0.010899+33.49083i | [12 empty] | 32.4 | 34.1545
[37 empty] | f: |  | frequency | [18 empty] | 32 | 0.0001-0.843646i | 0.000000001 | 0.010799+34.555756i | 5399336805.55556+0.0001i |  | 0.010799001+34.555756i | 58307443.559076+186578165214.597i | 5399336805.56636+34.555856i | 0.010799+34.555756i | 0.010899+33.71211i | [12 empty] | 32.6 | 34.3756
[37 empty] | HL: |  | Tuning Reactor Henry rating (millihenries) | [18 empty] | 32.2 | 0.0001-0.838406i | 0.000000001 | 0.010799+34.771729i | 5399336805.55556+0.0001i |  | 0.010799001+34.771729i | 58307443.559054+187744276182.504i | 5399336805.56636+34.771829i | 0.010799+34.771729i | 0.010899+33.933323i | [12 empty] | 32.8 | 34.5966
[37 empty] | IRATED FUNDAMENTAL : |  | Fundamental current rating of filter bank | [18 empty] | 32.4 | 0.0001-0.833231i | 0.000000001 | 0.010799+34.987703i | 5399336805.55556+0.0001i |  | 0.010799001+34.987703i | 58307443.559033+188910392549.747i | 5399336805.56636+34.987803i | 0.010799+34.987703i | 0.010899+34.154472i | [12 empty] | 33 | 34.8175
[36 empty] | VCAP FUNDAMENTAL VOLTAGE: |  |  | Fundamental voltage drop across capacitor | [18 empty] | 32.6 | 0.0001-0.828119i | 0.000000001 | 0.010799+35.203676i | 5399336805.55556+0.0001i |  | 0.010799001+35.203676i | 58307443.559011+190076503517.653i | 5399336805.56636+35.203776i | 0.010799+35.203676i | 0.010899+34.375557i | [12 empty] | 33.2 | 35.0384
[37 empty] | VCAP HARMONIC VOLTAGE: |  | Harmonic voltage drop across capacitor | [18 empty] | 32.8 | 0.0001-0.82307i | 0.000000001 | 0.010799+35.419649i | 5399336805.55556+0.0001i |  | 0.010799001+35.419649i | 58307443.558989+191242614485.559i | 5399336805.56636+35.419749i | 0.010799+35.419649i | 0.010899+34.596579i | [12 empty] | 33.4 | 35.2593
| 🧮 FORMULAS | [35 empty] | VCAP RMS VOLTAGE: |  | Capacitor RMS voltage (fundamental voltage + harmonic voltages) | [18 empty] | 33 | 0.0001-0.818081i | 0.000000001 | 0.010799+35.635623i | 5399336805.55556+0.0001i |  | 0.010799001+35.635623i | 58307443.558968+192408730852.802i | 5399336805.56636+35.635723i | 0.010799+35.635623i | 0.010899+34.817542i | [12 empty] | 33.6 | 35.4801
[37 empty] | VPEAK CAP VOLTAGE: |  | Capacitor voltage assuming or harmonics are coincident | [18 empty] | 33.2 | 0.0001-0.813153i | 0.000000001 | 0.010799+35.851596i | 5399336805.55556+0.0001i |  | 0.010799001+35.851596i | 58307443.558946+193574841820.708i | 5399336805.56636+35.851696i | 0.010799+35.851596i | 0.010899+35.038443i | [12 empty] | 33.8 | 35.7008
| The below shows how a 1000 kvar 13.8kV 4.7th tuned Notch Type Filter Design is computed manually and is the basis this spreadsheet. | [36 empty] | VCAP MAIN RMS VOLTAGE: | Capacitor RMS voltage including harmonics | [18 empty] | 33.4 | 0.0001-0.808284i | 0.000000001 | 0.010799+36.06757i | 5399336805.55556+0.0001i |  | 0.010799001+36.06757i | 58307443.558925+194740958187.952i | 5399336805.56636+36.06767i | 0.010799+36.06757i | 0.010899+35.259286i | [12 empty] | 34 | 35.9215
[38 empty] | VCAP MAIN, PEAK CAP VOLTAGE: | Capacitor peak voltage, including harmonics, and assuming peaks are in phase. | [18 empty] | 33.6 | 0.0001-0.803473i | 0.000000001 | 0.010799+36.283543i | 5399336805.55556+0.0001i |  | 0.010799001+36.283543i | 58307443.558903+195907069155.858i | 5399336805.56636+36.283643i | 0.010799+36.283543i | 0.010899+35.48007i | [12 empty] | 34.2 | 36.1421
[37 empty] | N: |  | Number of capacitors per phase | [18 empty] | 33.8 | 0.0001-0.798718i | 0.000000001 | 0.010799+36.499517i | 5399336805.55556+0.0001i |  | 0.010799001+36.499517i | 58307443.558881+197073185523.101i | 5399336805.56636+36.499617i | 0.010799+36.499517i | 0.010899+35.700799i | [12 empty] | 34.4 | 36.3627
[37 empty] | VCAP VAR RATING: |  | Capacitor can var rating (in Kvar) | [18 empty] | 34 | 0.0001-0.79402i | 0.000000001 | 0.010799+36.71549i | 5399336805.55556+0.0001i |  | 0.010799001+36.71549i | 58307443.55886+198239296491.007i | 5399336805.56636+36.71559i | 0.010799+36.71549i | 0.010899+35.92147i | [12 empty] | 34.6 | 36.5832
[37 empty] | ICAP RMS CURRENT: |  | RMS current seen by capacitor (amps rms) | [18 empty] | 34.2 | 0.0001-0.789377i | 0.000000001 | 0.010799+36.931464i | 5399336805.55556+0.0001i |  | 0.010799001+36.931464i | 58307443.558838+199405412858.25i | 5399336805.56636+36.931564i | 0.010799+36.931464i | 0.010899+36.142087i | [12 empty] | 34.8 | 36.8036
[37 empty] | IFILTER RMS CURRENT: |  | RMS current into filter branch (amps rms) | [18 empty] | 34.4 | 0.0001-0.784787i | 0.000000001 | 0.010799+37.147437i | 5399336805.55556+0.0001i |  | 0.010799001+37.147437i | 58307443.558817+200571523826.156i | 5399336805.56636+37.147537i | 0.010799+37.147437i | 0.010899+36.36265i | [12 empty] | 35 | 37.024
[37 empty] | In |  | Current in amps at each harmonic | [18 empty] | 34.6 | 0.0001-0.780251i | 0.000000001 | 0.010799+37.363411i | 5399336805.55556+0.0001i |  | 0.010799001+37.363411i | 58307443.558795+201737640193.399i | 5399336805.56636+37.363511i | 0.010799+37.363411i | 0.010899+36.58316i | [12 empty] | 35.2 | 37.2444
[58 empty] | 34.8 | 0.0001-0.775767i | 0.000000001 | 0.010799+37.579384i | 5399336805.55556+0.0001i |  | 0.010799001+37.579384i | 58307443.558773+202903751161.306i | 5399336805.56636+37.579484i | 0.010799+37.579384i | 0.010899+36.803617i | [12 empty] | 35.4 | 37.4647
[35 empty] | Disclaimer and Use Limitation | [22 empty] | 35 | 0.0001-0.771334i | 0.000000001 | 0.010799+37.795358i | 5399336805.55556+0.0001i |  | 0.010799001+37.795358i | 58307443.558752+204069867528.549i | 5399336805.56636+37.795458i | 0.010799+37.795358i | 0.010899+37.024024i | [12 empty] | 35.6 | 37.6849
[35 empty] | This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool. | [22 empty] | 35.2 | 0.0001-0.766951i | 0.000000001 | 0.010799+38.011331i | 5399336805.55556+0.0001i |  | 0.010799001+38.011331i | 58307443.55873+205235978496.455i | 5399336805.56636+38.011431i | 0.010799+38.011331i | 0.010899+37.24438i | [12 empty] | 35.8 | 37.9052
[58 empty] | 35.4 | 0.0001-0.762618i | 0.000000001 | 0.010799+38.227305i | 5399336805.55556+0.0001i |  | 0.010799001+38.227305i | 58307443.558709+206402094863.698i | 5399336805.56636+38.227405i | 0.010799+38.227305i | 0.010899+37.464687i | [12 empty] | 36 | 38.1253
[58 empty] | 35.6 | 0.0001-0.758334i | 0.000000001 | 0.010799+38.443278i | 5399336805.55556+0.0001i |  | 0.010799001+38.443278i | 58307443.558687+207568205831.604i | 5399336805.56636+38.443378i | 0.010799+38.443278i | 0.010899+37.684944i | [12 empty] | 36.2 | 38.3454
[58 empty] | 35.8 | 0.0001-0.754097i | 0.000000001 | 0.010799+38.659252i | 5399336805.55556+0.0001i |  | 0.010799001+38.659252i | 58307443.558665+208734322198.847i | 5399336805.56636+38.659352i | 0.010799+38.659252i | 0.010899+37.905155i | [12 empty] | 36.4 | 38.5655
[58 empty] | 36 | 0.0001-0.749908i | 0.000000001 | 0.010799+38.875225i | 5399336805.55556+0.0001i |  | 0.010799001+38.875225i | 58307443.558644+209900433166.754i | 5399336805.56636+38.875325i | 0.010799+38.875225i | 0.010899+38.125317i | [12 empty] | 36.6 | 38.7855
[58 empty] | 36.2 | 0.0001-0.745765i | 0.000000001 | 0.010799+39.091198i | 5399336805.55556+0.0001i |  | 0.010799001+39.091198i | 58307443.558622+211066544134.66i | 5399336805.56636+39.091298i | 0.010799+39.091198i | 0.010899+38.345433i | [12 empty] | 36.8 | 39.0055
[58 empty] | 36.4 | 0.0001-0.741667i | 0.000000001 | 0.010799+39.307172i | 5399336805.55556+0.0001i |  | 0.010799001+39.307172i | 58307443.558601+212232660501.903i | 5399336805.56636+39.307272i | 0.010799+39.307172i | 0.010899+38.565505i | [12 empty] | 37 | 39.2255
| One-Line Diagram Notch Type Filter Design Parameters | [56 empty] | 36.6 | 0.0001-0.737614i | 0.000000001 | 0.010799+39.523145i | 5399336805.55556+0.0001i |  | 0.010799001+39.523145i | 58307443.558579+213398771469.809i | 5399336805.56636+39.523245i | 0.010799+39.523145i | 0.010899+38.785531i | [12 empty] | 37.2 | 39.4454
[58 empty] | 36.8 | 0.0001-0.733606i | 0.000000001 | 0.010799+39.739119i | 5399336805.55556+0.0001i |  | 0.010799001+39.739119i | 58307443.558557+214564887837.052i | 5399336805.56636+39.739219i | 0.010799+39.739119i | 0.010899+39.005513i | [12 empty] | 37.4 | 39.6652
[58 empty] | 37 | 0.0001-0.72964i | 0.000000001 | 0.010799+39.955092i | 5399336805.55556+0.0001i |  | 0.010799001+39.955092i | 58307443.558536+215730998804.959i | 5399336805.56636+39.955192i | 0.010799+39.955092i | 0.010899+39.225452i | [12 empty] | 37.6 | 39.885
[58 empty] | 37.2 | 0.0001-0.725717i | 0.000000001 | 0.010799+40.171066i | 5399336805.55556+0.0001i |  | 0.010799001+40.171066i | 58307443.558514+216897115172.202i | 5399336805.56636+40.171166i | 0.010799+40.171066i | 0.010899+39.445349i | [12 empty] | 37.8 | 40.1048
[58 empty] | 37.4 | 0.0001-0.721836i | 0.000000001 | 0.010799+40.387039i | 5399336805.55556+0.0001i |  | 0.010799001+40.387039i | 58307443.558493+218063226140.108i | 5399336805.56636+40.387139i | 0.010799+40.387039i | 0.010899+39.665203i | [12 empty] | 38 | 40.3245
[58 empty] | 37.6 | 0.0001-0.717997i | 0.000000001 | 0.010799+40.603013i | 5399336805.55556+0.0001i |  | 0.010799001+40.603013i | 58307443.558471+219229342507.351i | 5399336805.56636+40.603113i | 0.010799+40.603013i | 0.010899+39.885016i | [12 empty] | 38.2 | 40.5442
[58 empty] | 37.8 | 0.0001-0.714198i | 0.000000001 | 0.010799+40.818986i | 5399336805.55556+0.0001i |  | 0.010799001+40.818986i | 58307443.558449+220395453475.257i | 5399336805.56636+40.819086i | 0.010799+40.818986i | 0.010899+40.104788i | [12 empty] | 38.4 | 40.7639
[58 empty] | 38 | 0.0001-0.710439i | 0.000000001 | 0.010799+41.03496i | 5399336805.55556+0.0001i |  | 0.010799001+41.03496i | 58307443.558428+221561569842.5i | 5399336805.56636+41.03506i | 0.010799+41.03496i | 0.010899+40.324521i | [12 empty] | 38.6 | 40.9835
[58 empty] | 38.2 | 0.0001-0.706719i | 0.000000001 | 0.010799+41.250933i | 5399336805.55556+0.0001i |  | 0.010799001+41.250933i | 58307443.558406+222727680810.406i | 5399336805.56636+41.251033i | 0.010799+41.250933i | 0.010899+40.544214i | [12 empty] | 38.8 | 41.2031
|  | Info@VarStec.com | [31 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 8 ¦ P a g e |  |  |  |  | 38.4 | 0.0001-0.703039i | 0.000000001 | 0.010799+41.466907i | 5399336805.55556+0.0001i |  | 0.010799001+41.466907i | 58307443.558385+223893797177.649i | 5399336805.56636+41.467007i | 0.010799+41.466907i | 0.010899+40.763868i | [12 empty] | 39 | 41.4226
[58 empty] | 38.6 | 0.0001-0.699396i | 0.000000001 | 0.010799+41.68288i | 5399336805.55556+0.0001i |  | 0.010799001+41.68288i | 58307443.558363+225059908145.556i | 5399336805.56636+41.68298i | 0.010799+41.68288i | 0.010899+40.983484i | [12 empty] | 39.2 | 41.6421
[58 empty] | 38.8 | 0.0001-0.695791i | 0.000000001 | 0.010799+41.898854i | 5399336805.55556+0.0001i |  | 0.010799001+41.898854i | 58307443.558341+226226024512.799i | 5399336805.56636+41.898954i | 0.010799+41.898854i | 0.010899+41.203063i | [12 empty] | 39.4 | 41.8616
[58 empty] | 39 | 0.0001-0.692223i | 0.000000001 | 0.010799+42.114827i | 5399336805.55556+0.0001i |  | 0.010799001+42.114827i | 58307443.55832+227392135480.705i | 5399336805.56636+42.114927i | 0.010799+42.114827i | 0.010899+41.422604i | [12 empty] | 39.6 | 42.081
[58 empty] | 39.2 | 0.0001-0.688691i | 0.000000001 | 0.010799+42.330801i | 5399336805.55556+0.0001i |  | 0.010799001+42.330801i | 58307443.558298+228558251847.948i | 5399336805.56636+42.330901i | 0.010799+42.330801i | 0.010899+41.64211i | [12 empty] | 39.8 | 42.3004
[58 empty] | 39.4 | 0.0001-0.685195i | 0.000000001 | 0.010799+42.546774i | 5399336805.55556+0.0001i |  | 0.010799001+42.546774i | 58307443.558277+229724362815.854i | 5399336805.56636+42.546874i | 0.010799+42.546774i | 0.010899+41.861579i | [12 empty] | 40 | 42.5198
[58 empty] | 39.6 | 0.0001-0.681734i | 0.000000001 | 0.010799+42.762748i | 5399336805.55556+0.0001i |  | 0.010799001+42.762748i | 58307443.558255+230890479183.097i | 5399336805.56636+42.762848i | 0.010799+42.762748i | 0.010899+42.081014i | [12 empty] | 40.2 | 42.7391
[58 empty] | 39.8 | 0.0001-0.678309i | 0.000000001 | 0.010799+42.978721i | 5399336805.55556+0.0001i |  | 0.010799001+42.978721i | 58307443.558233+232056590151.004i | 5399336805.56636+42.978821i | 0.010799+42.978721i | 0.010899+42.300412i | [12 empty] | 40.4 | 42.9584
[58 empty] | 40 | 0.0001-0.674917i | 0.000000001 | 0.010799+43.194694i | 5399336805.55556+0.0001i |  | 0.010799001+43.194694i | 58307443.558212+233222701118.91i | 5399336805.56636+43.194794i | 0.010799+43.194694i | 0.010899+42.519777i | [12 empty] | 40.6 | 43.1777
[58 empty] | 40.2 | 0.0001-0.671559i | 0.000000001 | 0.010799+43.410668i | 5399336805.55556+0.0001i |  | 0.010799001+43.410668i | 58307443.55819+234388817486.153i | 5399336805.56636+43.410768i | 0.010799+43.410668i | 0.010899+42.739109i | [12 empty] | 40.8 | 43.3969
[58 empty] | 40.4 | 0.0001-0.668235i | 0.000000001 | 0.010799+43.626641i | 5399336805.55556+0.0001i |  | 0.010799001+43.626641i | 58307443.558169+235554928454.059i | 5399336805.56636+43.626741i | 0.010799+43.626641i | 0.010899+42.958406i | [12 empty] | 41 | 43.6161
[58 empty] | 40.6 | 0.0001-0.664943i | 0.000000001 | 0.010799+43.842615i | 5399336805.55556+0.0001i |  | 0.010799001+43.842615i | 58307443.558147+236721044821.302i | 5399336805.56636+43.842715i | 0.010799+43.842615i | 0.010899+43.177672i | [12 empty] | 41.2 | 43.8353
[58 empty] | 40.8 | 0.0001-0.661683i | 0.000000001 | 0.010799+44.058588i | 5399336805.55556+0.0001i |  | 0.010799001+44.058588i | 58307443.558125+237887155789.209i | 5399336805.56636+44.058688i | 0.010799+44.058588i | 0.010899+43.396905i | [12 empty] | 41.4 | 44.0544
[58 empty] | 41 | 0.0001-0.658456i | 0.000000001 | 0.010799+44.274562i | 5399336805.55556+0.0001i |  | 0.010799001+44.274562i | 58307443.558104+239053272156.452i | 5399336805.56636+44.274662i | 0.010799+44.274562i | 0.010899+43.616106i | [12 empty] | 41.6 | 44.2735
[58 empty] | 41.2 | 0.0001-0.655259i | 0.000000001 | 0.010799+44.490535i | 5399336805.55556+0.0001i |  | 0.010799001+44.490535i | 58307443.558082+240219383124.358i | 5399336805.56636+44.490635i | 0.010799+44.490535i | 0.010899+43.835276i | [12 empty] | 41.8 | 44.4926
[58 empty] | 41.4 | 0.0001-0.652094i | 0.000000001 | 0.010799+44.706509i | 5399336805.55556+0.0001i |  | 0.010799001+44.706509i | 58307443.558061+241385499491.601i | 5399336805.56636+44.706609i | 0.010799+44.706509i | 0.010899+44.054415i | [12 empty] | 42 | 44.7117
[58 empty] | 41.6 | 0.0001-0.648959i | 0.000000001 | 0.010799+44.922482i | 5399336805.55556+0.0001i |  | 0.010799001+44.922482i | 58307443.558039+242551610459.507i | 5399336805.56636+44.922582i | 0.010799+44.922482i | 0.010899+44.273523i | [12 empty] | 42.2 | 44.9307
[58 empty] | 41.8 | 0.0001-0.645854i | 0.000000001 | 0.010799+45.138456i | 5399336805.55556+0.0001i |  | 0.010799001+45.138456i | 58307443.558018+243717726826.75i | 5399336805.56636+45.138556i | 0.010799+45.138456i | 0.010899+44.492602i | [12 empty] | 42.4 | 45.1497
[58 empty] | 42 | 0.0001-0.642778i | 0.000000001 | 0.010799+45.354429i | 5399336805.55556+0.0001i |  | 0.010799001+45.354429i | 58307443.557996+244883837794.656i | 5399336805.56636+45.354529i | 0.010799+45.354429i | 0.010899+44.711651i | [12 empty] | 42.6 | 45.3686
[58 empty] | 42.2 | 0.0001-0.639732i | 0.000000001 | 0.010799+45.570403i | 5399336805.55556+0.0001i |  | 0.010799001+45.570403i | 58307443.557974+246049954161.9i | 5399336805.56636+45.570503i | 0.010799+45.570403i | 0.010899+44.930671i | [12 empty] | 42.8 | 45.5876
[58 empty] | 42.4 | 0.0001-0.636714i | 0.000000001 | 0.010799+45.786376i | 5399336805.55556+0.0001i |  | 0.010799001+45.786376i | 58307443.557953+247216065129.806i | 5399336805.56636+45.786476i | 0.010799+45.786376i | 0.010899+45.149662i | [12 empty] | 43 | 45.8065
[58 empty] | 42.6 | 0.0001-0.633725i | 0.000000001 | 0.010799+46.00235i | 5399336805.55556+0.0001i |  | 0.010799001+46.00235i | 58307443.557931+248382181497.049i | 5399336805.56636+46.00245i | 0.010799+46.00235i | 0.010899+45.368625i | [12 empty] | 43.2 | 46.0253
[58 empty] | 42.8 | 0.0001-0.630764i | 0.000000001 | 0.010799+46.218323i | 5399336805.55556+0.0001i |  | 0.010799001+46.218323i | 58307443.55791+249548292464.955i | 5399336805.56636+46.218423i | 0.010799+46.218323i | 0.010899+45.587559i | [12 empty] | 43.4 | 46.2442
[58 empty] | 43 | 0.0001-0.62783i | 0.000000001 | 0.010799+46.434297i | 5399336805.55556+0.0001i |  | 0.010799001+46.434297i | 58307443.557888+250714408832.198i | 5399336805.56636+46.434397i | 0.010799+46.434297i | 0.010899+45.806467i | [12 empty] | 43.6 | 46.463
[58 empty] | 43.2 | 0.0001-0.624923i | 0.000000001 | 0.010799+46.65027i | 5399336805.55556+0.0001i |  | 0.010799001+46.65027i | 58307443.557866+251880519800.104i | 5399336805.56636+46.65037i | 0.010799+46.65027i | 0.010899+46.025347i | [12 empty] | 43.8 | 46.6818
[58 empty] | 43.4 | 0.0001-0.622043i | 0.000000001 | 0.010799+46.866243i | 5399336805.55556+0.0001i |  | 0.010799001+46.866243i | 58307443.557845+253046630768.011i | 5399336805.56636+46.866343i | 0.010799+46.866243i | 0.010899+46.2442i | [12 empty] | 44 | 46.9006
[58 empty] | 43.6 | 0.0001-0.61919i | 0.000000001 | 0.010799+47.082217i | 5399336805.55556+0.0001i |  | 0.010799001+47.082217i | 58307443.557823+254212747135.254i | 5399336805.56636+47.082317i | 0.010799+47.082217i | 0.010899+46.463027i | [12 empty] | 44.2 | 47.1194
[58 empty] | 43.8 | 0.0001-0.616363i | 0.000000001 | 0.010799+47.29819i | 5399336805.55556+0.0001i |  | 0.010799001+47.29819i | 58307443.557802+255378858103.16i | 5399336805.56636+47.29829i | 0.010799+47.29819i | 0.010899+46.681827i | [12 empty] | 44.4 | 47.3381
[58 empty] | 44 | 0.0001-0.613561i | 0.000000001 | 0.010799+47.514164i | 5399336805.55556+0.0001i |  | 0.010799001+47.514164i | 58307443.55778+256544974470.403i | 5399336805.56636+47.514264i | 0.010799+47.514164i | 0.010899+46.900603i | [12 empty] | 44.6 | 47.5568
[58 empty] | 44.2 | 0.0001-0.610785i | 0.000000001 | 0.010799+47.730137i | 5399336805.55556+0.0001i |  | 0.010799001+47.730137i | 58307443.557758+257711085438.309i | 5399336805.56636+47.730237i | 0.010799+47.730137i | 0.010899+47.119352i | [12 empty] | 44.8 | 47.7755
[58 empty] | 44.4 | 0.0001-0.608033i | 0.000000001 | 0.010799+47.946111i | 5399336805.55556+0.0001i |  | 0.010799001+47.946111i | 58307443.557737+258877201805.552i | 5399336805.56636+47.946211i | 0.010799+47.946111i | 0.010899+47.338078i | [12 empty] | 45 | 47.9941
[58 empty] | 44.6 | 0.0001-0.605307i | 0.000000001 | 0.010799+48.162084i | 5399336805.55556+0.0001i |  | 0.010799001+48.162084i | 58307443.557715+260043312773.459i | 5399336805.56636+48.162184i | 0.010799+48.162084i | 0.010899+47.556777i | [12 empty] | 45.2 | 48.2127
[58 empty] | 44.8 | 0.0001-0.602605i | 0.000000001 | 0.010799+48.378058i | 5399336805.55556+0.0001i |  | 0.010799001+48.378058i | 58307443.557694+261209429140.702i | 5399336805.56636+48.378158i | 0.010799+48.378058i | 0.010899+47.775453i | [12 empty] | 45.4 | 48.4313
[58 empty] | 45 | 0.0001-0.599926i | 0.000000001 | 0.010799+48.594031i | 5399336805.55556+0.0001i |  | 0.010799001+48.594031i | 58307443.557672+262375540108.608i | 5399336805.56636+48.594131i | 0.010799+48.594031i | 0.010899+47.994105i | [12 empty] | 45.6 | 48.6499
[58 empty] | 45.2 | 0.0001-0.597272i | 0.000000001 | 0.010799+48.810005i | 5399336805.55556+0.0001i |  | 0.010799001+48.810005i | 58307443.55765+263541656475.851i | 5399336805.56636+48.810105i | 0.010799+48.810005i | 0.010899+48.212733i | [12 empty] | 45.8 | 48.8685
[58 empty] | 45.4 | 0.0001-0.594641i | 0.000000001 | 0.010799+49.025978i | 5399336805.55556+0.0001i |  | 0.010799001+49.025978i | 58307443.557629+264707767443.757i | 5399336805.56636+49.026078i | 0.010799+49.025978i | 0.010899+48.431337i | [12 empty] | 46 | 49.087
[58 empty] | 45.6 | 0.0001-0.592033i | 0.000000001 | 0.010799+49.241952i | 5399336805.55556+0.0001i |  | 0.010799001+49.241952i | 58307443.557607+265873883811i | 5399336805.56636+49.242052i | 0.010799+49.241952i | 0.010899+48.649919i | [12 empty] | 46.2 | 49.3055
[58 empty] | 45.8 | 0.0001-0.589447i | 0.000000001 | 0.010799+49.457925i | 5399336805.55556+0.0001i |  | 0.010799001+49.457925i | 58307443.557586+267039994778.906i | 5399336805.56636+49.458025i | 0.010799+49.457925i | 0.010899+48.868478i | [12 empty] | 46.4 | 49.524
[58 empty] | 46 | 0.0001-0.586884i | 0.000000001 | 0.010799+49.673899i | 5399336805.55556+0.0001i |  | 0.010799001+49.673899i | 58307443.557564+268206111146.15i | 5399336805.56636+49.673999i | 0.010799+49.673899i | 0.010899+49.087015i | [12 empty] | 46.6 | 49.7425
[58 empty] | 46.2 | 0.0001-0.584344i | 0.000000001 | 0.010799+49.889872i | 5399336805.55556+0.0001i |  | 0.010799001+49.889872i | 58307443.557542+269372222114.056i | 5399336805.56636+49.889972i | 0.010799+49.889872i | 0.010899+49.305528i | [12 empty] | 46.8 | 49.9609
[58 empty] | 46.4 | 0.0001-0.581825i | 0.000000001 | 0.010799+50.105846i | 5399336805.55556+0.0001i |  | 0.010799001+50.105846i | 58307443.557521+270538338481.299i | 5399336805.56636+50.105946i | 0.010799+50.105846i | 0.010899+49.524021i | [12 empty] | 47 | 50.1794
[58 empty] | 46.6 | 0.0001-0.579328i | 0.000000001 | 0.010799+50.321819i | 5399336805.55556+0.0001i |  | 0.010799001+50.321819i | 58307443.557499+271704449449.205i | 5399336805.56636+50.321919i | 0.010799+50.321819i | 0.010899+49.742491i | [12 empty] | 47.2 | 50.3978
[58 empty] | 46.8 | 0.0001-0.576852i | 0.000000001 | 0.010799+50.537793i | 5399336805.55556+0.0001i |  | 0.010799001+50.537793i | 58307443.557478+272870565816.448i | 5399336805.56636+50.537893i | 0.010799+50.537793i | 0.010899+49.960941i | [12 empty] | 47.4 | 50.6162
[58 empty] | 47 | 0.0001-0.574398i | 0.000000001 | 0.010799+50.753766i | 5399336805.55556+0.0001i |  | 0.010799001+50.753766i | 58307443.557456+274036676784.354i | 5399336805.56636+50.753866i | 0.010799+50.753766i | 0.010899+50.179368i | [12 empty] | 47.6 | 50.8345
[58 empty] | 47.2 | 0.0001-0.571964i | 0.000000001 | 0.010799+50.969739i | 5399336805.55556+0.0001i |  | 0.010799001+50.969739i | 58307443.557434+275202787752.261i | 5399336805.56636+50.969839i | 0.010799+50.969739i | 0.010899+50.397775i | [12 empty] | 47.8 | 51.0529
[58 empty] | 47.4 | 0.0001-0.56955i | 0.000000001 | 0.010799+51.185713i | 5399336805.55556+0.0001i |  | 0.010799001+51.185713i | 58307443.557413+276368904119.504i | 5399336805.56636+51.185813i | 0.010799+51.185713i | 0.010899+50.616163i | [12 empty] | 48 | 51.2712
[58 empty] | 47.6 | 0.0001-0.567157i | 0.000000001 | 0.010799+51.401686i | 5399336805.55556+0.0001i |  | 0.010799001+51.401686i | 58307443.557391+277535015087.41i | 5399336805.56636+51.401786i | 0.010799+51.401686i | 0.010899+50.834529i | [12 empty] | 48.2 | 51.4895
[58 empty] | 47.8 | 0.0001-0.564784i | 0.000000001 | 0.010799+51.61766i | 5399336805.55556+0.0001i |  | 0.010799001+51.61766i | 58307443.55737+278701131454.653i | 5399336805.56636+51.61776i | 0.010799+51.61766i | 0.010899+51.052876i | [12 empty] | 48.4 | 51.7078
[58 empty] | 48 | 0.0001-0.562431i | 0.000000001 | 0.010799+51.833633i | 5399336805.55556+0.0001i |  | 0.010799001+51.833633i | 58307443.557348+279867242422.559i | 5399336805.56636+51.833733i | 0.010799+51.833633i | 0.010899+51.271202i | [12 empty] | 48.6 | 51.9261
[58 empty] | 48.2 | 0.0001-0.560097i | 0.000000001 | 0.010799+52.049607i | 5399336805.55556+0.0001i |  | 0.010799001+52.049607i | 58307443.557326+281033358789.802i | 5399336805.56636+52.049707i | 0.0108+52.049607i | 0.0109+51.48951i | [12 empty] | 48.8 | 52.1443
[58 empty] | 48.4 | 0.0001-0.557783i | 0.000000001 | 0.010799+52.26558i | 5399336805.55556+0.0001i |  | 0.010799001+52.26558i | 58307443.557305+282199469757.709i | 5399336805.56636+52.26568i | 0.0108+52.26558i | 0.0109+51.707797i | [12 empty] | 49 | 52.3625
[58 empty] | 48.6 | 0.0001-0.555487i | 0.000000001 | 0.010799+52.481554i | 5399336805.55556+0.0001i |  | 0.010799001+52.481554i | 58307443.557283+283365586124.952i | 5399336805.56636+52.481654i | 0.0108+52.481554i | 0.0109+51.926067i | [12 empty] | 49.2 | 52.5808
[58 empty] | 48.8 | 0.0001-0.553211i | 0.000000001 | 0.010799+52.697527i | 5399336805.55556+0.0001i |  | 0.010799001+52.697527i | 58307443.557262+284531697092.858i | 5399336805.56636+52.697627i | 0.0108+52.697527i | 0.0109+52.144316i | [12 empty] | 49.4 | 52.799
[58 empty] | 49 | 0.0001-0.550953i | 0.000000001 | 0.010799+52.913501i | 5399336805.55556+0.0001i |  | 0.010799001+52.913501i | 58307443.55724+285697813460.101i | 5399336805.56636+52.913601i | 0.0108+52.913501i | 0.0109+52.362548i | [12 empty] | 49.6 | 53.0171
[58 empty] | 49.2 | 0.0001-0.548713i | 0.000000001 | 0.010799+53.129474i | 5399336805.55556+0.0001i |  | 0.010799001+53.129474i | 58307443.557218+286863924428.007i | 5399336805.56636+53.129574i | 0.0108+53.129474i | 0.0109+52.580761i | [12 empty] | 49.8 | 53.2353
[58 empty] | 49.4 | 0.0001-0.546492i | 0.000000001 | 0.010799+53.345448i | 5399336805.55556+0.0001i |  | 0.010799001+53.345448i | 58307443.557197+288030040795.25i | 5399336805.56636+53.345548i | 0.0108+53.345448i | 0.0109+52.798956i | [12 empty] | 50 | 53.4534
[58 empty] | 49.6 | 0.0001-0.544288i | 0.000000001 | 0.010799+53.561421i | 5399336805.55556+0.0001i |  | 0.010799001+53.561421i | 58307443.557175+289196151763.156i | 5399336805.56636+53.561521i | 0.0108+53.561421i | 0.0109+53.017133i
[58 empty] | 49.8 | 0.0001-0.542102i | 0.000000001 | 0.010799+53.777395i | 5399336805.55556+0.0001i |  | 0.010799001+53.777395i | 58307443.557154+290362268130.4i | 5399336805.56636+53.777495i | 0.0108+53.777395i | 0.0109+53.235293i
[58 empty] | 50 | 0.0001-0.539934i | 0.000000001 | 0.010799+53.993368i | 5399336805.55556+0.0001i |  | 0.010799001+53.993368i | 58307443.557132+291528379098.306i | 5399336805.56636+53.993468i | 0.0108+53.993368i | 0.0109+53.453434i
[62 empty] | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | 9.96
[60 empty] | VCAP HARMONIC VOLTAGE (volts)^2 |  | 56376516.1461 | 0 | 0 | 0 | 291528.3794 | 95192.9402 | 21683.929 | 4624 | 1008.7487 | 201.8895 | 137.7733 | 116.6114 | 0 | 0 | 59.4956 | 53.2375
[60 empty] | Filter Current (amps) (In)^2 |  | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 14.0834
[60 empty] | kvar (single phase) |  | 2088.2756 | 0 | 0 | 0 | 53.9934 | 24.6827 | 8.8353 | 1.869 | 0.63522 | 0.14209 | 0.11738 | 0.10799 | 0 | 0 | 0.077133 | 0.072964 | 73.7868
3674.5846
[60 empty] | harmonic # |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37
[60 empty] | Total filter amps |  | 278.1241 | 0 | 0 | 0 | 100 | 80 | 60 | 30 | 20 | 10 | 10 | 10 | 0 | 0 | 10 | 10
[60 empty] | R & X EQUIVALENT IMPEDANCE (ohms) |  | 1.0799 | 2.1597 | 3.2396 | 4.3195 | 5.3993 | 7.5591 | 11.8785 | 14.0383 | 18.3577 | 20.5175 | 24.8369 | 26.9967 | 31.3162 | 33.4759 | 37.7954 | 39.9551
[60 empty] | I REACTOR (Calculate voltage then divide by xLn) |  | 278.1241 | 0 | 0 | 0 | 100 | 80 | 60 | 30 | 20 | 10 | 10 | 10 | 0 | 0 | 10 | 10
[60 empty] | I RESISTOR (calculate voltage then divide by R) |  | 5.5625e-08 | 0 | 0 | 0 | 1e-07 | 1.12e-07 | 1.32e-07 | 7.8e-08 | 6.8e-08 | 3.8e-08 | 4.6e-08 | 5e-08 | 0 | 0 | 7e-08 | 7.4e-08
[60 empty] | Resistor losses (watts) |  | 1.6706e-05 | 0 | 0 | 0 | 5.3993e-05 | 6.7729e-05 | 9.4078e-05 | 3.285e-05 | 2.4967e-05 | 7.7966e-06 | 1.1425e-05 | 1.3498e-05 | 0 | 0 | 2.6457e-05 | 2.9567e-05 | 0.00036236 | 0.0010871
[60 empty] | I Resistor ^2 (watts) |  | 3.0941e-15 | 0 | 0 | 0 | 1e-14 | 1.2544e-14 | 1.7424e-14 | 6.084e-15 | 4.624e-15 | 1.444e-15 | 2.116e-15 | 2.5e-15 | 0 | 0 | 4.9e-15 | 5.476e-15 | Resistor RMS Amps |  | 2.6496e-07
[60 empty] | Total filter amps^2 |  | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | Total Filter RMS Amps |  | 314.8858
[60 empty] | I2R REACTOR LOSSES (watts) |  | 835.3102 | 0 | 0 | 0 | 107.9867 | 69.1115 | 38.8752 | 9.7188 | 4.3195 | 1.0799 | 1.0799 | 1.0799 | 0 | 0 | 1.0799 | 1.0799
[61 empty] | Reactor Current Squared | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 314.8858
This spreadsheet is used to support the design, tuning, and component selection associated with Notch type harmonic filters as engineered by VarStec Power Solutions. It provides a consistent methodology for determining all electrical parameters required for proper filter performance, including reactances, inductance, capacitor reactive power and voltage ratings, harmonic currents, voltage stresses, and damping resistance. The summary below describes the calculation process applied throughout the tool using a 13.8kV 1000 kvar filter branch as an example. The tool assumes that harmonic simulations have been conducted and that the current spectrum into the harmonic filter is known. These values are inserted in the blue highlighted fields of rows 24 and 25 on page 1. For additional information, engineering support, or custom filter designs, contact VarStec Power Solutions at info@varstec.com. The design process begins by establishing the fundamental kvar requirement of the harmonic filter, typically based on the kvar demand of the connected load or the kvar allocation assigned to each stage of a multi-stage harmonic filter. This requirement is defined as and forms the foundation of all subsequent calculations. Using the system’s nominal line-to-line voltage , the spreadsheet determines the fundamental filter reactance, . For a notch type filter, the summation of XC and XL must sum to this value where Xeff=XL-XC. Xc and determined using the tuning point and the relationship: .
This spreadsheet is used to support the design, tuning, and component selection associated with Notch type harmonic filters as engineered by VarStec Power Solutions. It provides a consistent methodology for determining all electrical parameters required for proper filter performance, including reactances, inductance, capacitor reactive power and voltage ratings, harmonic currents, voltage stresses, and damping resistance. The summary below describes the calculation process applied throughout the tool using a 13.8kV 1000 kvar filter branch as an example. The tool assumes that harmonic simulations have been conducted and that the current spectrum into the harmonic filter is known. These values are inserted in the blue highlighted fields of rows 24 and 25 on page 1. For additional information, engineering support, or custom filter designs, contact VarStec Power Solutions at info@varstec.com. The design process begins by establishing the fundamental kvar requirement of the harmonic filter, typically based on the kvar demand of the connected load or the kvar allocation assigned to each stage of a multi-stage harmonic filter. This requirement is defined as 𝑄_𝑒𝑓𝑓 and forms the foundation of all subsequent calculations. Using the system’s nominal line-to-line voltage 𝑘𝑉_𝐿𝐿𝑆𝑌𝑆, the spreadsheet determines the fundamental filter reactance, 𝑋_𝑒𝑓𝑓. For a notch type filter, the summation of XC and XL must sum to this value where Xeff=XL-XC. Xc and determined using the tuning point and the relationship: 𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓 .
The harmonic filter design must ensure capacitor operating duties stay within IEEE/IEC-rated limits, including the allowable 10% continuous overvoltage. The spreadsheet checks four key parameters against their rated duty: % Rated Volts, % Crest Voltage, % Amps, % kVAR. If any value exceeds its limit, the cell turns red. In that case, increase the capacitor voltage rating. The objective is to meet the required duty without significantly exceeding the rating, which would increase cost.
With XC known, XL is computed using the relationship: Xeff=XL-XC. From there L and C are calculated.
The capacitor kvar ratings is then determined using the rated operating voltage. With kvar and reactances established, the spreadsheet computes the fundamental filter current and applies injected harmonic current data to evaluate the resulting capacitor voltage stresses, current duty, and reactive power duty. These computed values are compared against industry-standard capacitor ratings to confirm suitability for the intended application.
Taken together, these calculations define a complete, consistent, and repeatable VarStec methodology for the engineering of notch type harmonic filters. The spreadsheet determines all critical design parameters, including reactances, inductance, kvar ratings, current loading, and voltage stress, using standardized electrical notation to provide traceability, transparency, and field-proven reliability.
(ohms) =
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/𝑄_𝑒𝑓𝑓 (ohms) = 〖13.8〗^2/(1.0 )=190.4 (𝑜ℎ𝑚𝑠)
(ohms) = 190.4 (ohms)=199.4 (ohms)
𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓 (ohms) = (〖4.7〗^2/(〖4.7〗^2−1)) 190.4 (ohms)=199.4 (ohms)
=
𝑋_𝐿=𝑋_𝐶/ℎ^2 = 199.4/〖4.7〗^2 =9.03 𝑜ℎ𝑚𝑠
= 23.95 mH
𝐻(𝑖𝑛𝑑𝑢𝑐𝑡𝑎𝑛𝑐𝑒)=𝑋_𝐿/2𝜋𝑓×1000(𝑚𝐻)=9.03/(2𝜋 60)×1000(𝑚𝐻)= 23.95 mH
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒𝐼_𝑛^2 )
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆 )×1000=1.0/(1.73×13.8)×1000=41.88 𝑎𝑚𝑝𝑠
〖𝑄_(𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸 (𝑀𝑉𝐴𝑅)) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶 =(9.54)^2/199.47=0.456 𝑀𝑉𝐴𝑅/𝑃ℎ𝑎𝑠𝑒〗_
𝑄_𝑒𝑓𝑓=𝑂𝑢𝑡𝑝𝑢𝑡 𝑀𝑉𝐴𝑅 𝑅𝑎𝑡𝑖𝑛𝑔 𝑜𝑓 𝐹𝑖𝑙𝑡𝑒𝑟=(𝐷𝑒𝑠𝑖𝑟𝑒𝑑 3 𝑃ℎ𝑎𝑠𝑒 𝑘𝑣𝑎𝑟)/1000 =1.0 𝑀𝑉𝐴𝑅
k
k𝑉_𝐿𝐿𝑆𝑌𝑆=𝐹𝑖𝑙𝑡𝑒𝑟 𝑁𝑜𝑚𝑖𝑛𝑎𝑙 𝐿𝑖𝑛𝑒−𝑡𝑜−𝐿𝑖𝑛𝑒 𝑉𝑜𝑙𝑡𝑎𝑔𝑒 𝑅𝑎𝑡𝑖𝑛𝑔 (𝐾𝑉)=13.8 𝑘𝑉
(f)
𝐶=1/(2𝜋𝑓𝑋_𝑐 ) (f)
𝐿=𝑋_𝐿/2𝜋𝑓 (𝐻)
VLN
JXL
-JXC

## HP Filter Design
[57 empty] | Impedance Calculations | [22 empty] | X
f
[33 empty] | VarStec Power Solutions, Inc. | [24 empty] | PLOT (ohms) |  |  | (res branch) |  | (aux branch) | Resistance x AUX Branch | RES Branch + AUX Branch | Parallel Sum of AUX and Resistance Branch | + Main Caps | [14 empty] | SD - Standard Duty Capacitors
[33 empty] | PO Box 942 | [23 empty] | HARM # | Xc main | Xc aux | XL (inductance) | Resistance |  | XCAUX + XL | [18 empty] | HD- Heavy Duty Capacitors
[33 empty] | Saratoga Springs, NY 12866 | Enter Customer PO # ¦ Stage 1 | [22 empty] | 1 | 0.0001-26.996684i | 0.000000001 | 0.010799+1.079867i | 10.798674+0.0001i |  | 0.010799+1.079867i | 0.116507+11.661133i | 10.809473+1.079967i | 0.117387+1.06706i | 0.117487-25.929624i |  | 1 | 415.1158 | 172321.1292 | [8 empty] | 1 | 25.9299 | EXD - Extreme Duty Capacitors
[33 empty] | 518.369.7589 | [23 empty] | 1.2 | 0.0001-22.497237i | 0.000000001 | 0.010799+1.295841i | 10.798674+0.0001i |  | 0.010799+1.295841i | 0.116485+13.993366i | 10.809473+1.295941i | 0.163627+1.274929i | 0.163727-21.222308i |  | 2 | 0 | 0 | [8 empty] | 1.2 | 21.2229
| Harmonic Filter Design / High-Pass (HP) Type | [32 empty] | 📐 DESIGN VERIFICATION | [22 empty] | 1.4 | 0.0001-19.283346i | 0.000000001 | 0.010799+1.511814i | 10.798674+0.0001i |  | 0.010799+1.511814i | 0.116464+16.325588i | 10.809473+1.511914i | 0.217759+1.479846i | 0.217859-17.8035i |  | 3 | 0 | 0 | [8 empty] | 1.4 | 17.8048 | DF (Damping Factor) | 300
[57 empty] | 1.6 | 0.0001-16.872928i | 0.000000001 | 0.010799+1.727788i | 10.798674+0.0001i |  | 0.010799+1.727788i | 0.116442+18.65782i | 10.809473+1.727888i | 0.279539+1.681378i | 0.279639-15.19155i |  | 4 | 0 | 0 | [8 empty] | 1.6 | 15.1941
| 📜 PROJECT DETAILS | [30 empty] | April 19, 2026 |  | Capacitor Design Ratings Versus Duty Rating | [22 empty] | 1.8 | 0.0001-14.998158i | 0.000000001 | 0.010799+1.943761i | 10.798674+0.0001i |  | 0.010799+1.943761i | 0.116421+20.990042i | 10.809473+1.943861i | 0.34869+1.879114i | 0.34879-13.119044i |  | 5 | 134.1641 | 18000 | [8 empty] | 1.8 | 13.1237
[41 empty] | Design Values | [15 empty] | 2 | 0.0001-13.498342i | 0.000000001 | 0.010799+2.159735i | 10.798674+0.0001i |  | 0.010799+2.159735i | 0.116399+23.322275i | 10.809473+2.159835i | 0.424909+2.072677i | 0.425009-11.425665i |  | 7 | 98.3078 | 9664.4295 | [8 empty] | 2 | 11.4336
|  |  |  | Project Name: | Enter Project Name | [16 empty] | VarStec SO #: |  | Enter SO Number | [16 empty] | At Nominal Voltage | [5 empty] | At Nominal 110% System Voltage | [9 empty] | 2.2 | 0.0001-12.27122i | 0.000000001 | 0.010799+2.375708i | 10.798674+0.0001i |  | 0.010799+2.375708i | 0.116377+25.654497i | 10.809473+2.375808i | 0.507866+2.261711i | 0.507966-10.009509i |  | 11 | 60.5406 | 3665.1584 | [8 empty] | 2.2 | 10.0224
|  |  |  | Customer PO #: | Enter Customer PO # | [16 empty] | Revision #: |  | Rev 1 | [10 empty] | Design Parameter | [12 empty] | Rated Duty | [8 empty] | 2.4 | 0.0001-11.248618i | 0.000000001 | 0.010799+2.591682i | 10.798674+0.0001i |  | 0.010799+2.591682i | 0.116356+27.98673i | 10.809473+2.591782i | 0.597216+2.445899i | 0.597316-8.802719i |  | 13 | 27.437 | 752.7881 | [8 empty] | 2.4 | 8.823
|  |  |  | Tag #: | Enter Tag Number | [16 empty] | Stage/Branch: |  | Stage 1 | [14 empty] | % RATED VOLTS: |  | 75.66% | [5 empty] | 83.18% | 125% | [8 empty] | 2.6 | 0.0001-10.38334i | 0.000000001 | 0.010799+2.807655i | 10.798674+0.0001i |  | 0.010799+2.807655i | 0.116334+30.318952i | 10.809473+2.807755i | 0.692592+2.62495i | 0.692692-7.75839i |  | 17 | 15.2106 | 231.3625 | [8 empty] | 2.6 | 7.7893
[39 empty] | % CREST VOLTAGE: |  | 86.85% | [5 empty] | 96.85% | 135% | [8 empty] | 2.8 | 0.0001-9.641673i | 0.000000001 | 0.010799+3.023629i | 10.798674+0.0001i |  | 0.010799+3.023629i | 0.116313+32.651185i | 10.809473+3.023729i | 0.793614+2.798611i | 0.793714-6.843062i |  | 19 | 6.9862 | 48.8069 | [8 empty] | 2.8 | 6.8889
| 🧮 SPECIFICATION DETAILS | [37 empty] | % 60HZ AMPS: |  | 85.35% | [5 empty] | 92.08% | 135% | [8 empty] | 3 | 0.0001-8.998895i | 0.000000001 | 0.010799+3.239602i | 10.798674+0.0001i |  | 0.010799+3.239602i | 0.116291+34.983407i | 10.809473+3.239702i | 0.899894+2.966659i | 0.899994-6.032236i |  | 23 | 5.9809 | 35.7711 | [8 empty] | 3 | 6.099
|  | Key Filter Ratings | [36 empty] | % 60HZ KVAR: |  | 59.29% | [5 empty] | 71.23% | 135% | [8 empty] | 3.2 | 0.0001-8.436464i | 0.000000001 | 0.010799+3.455576i | 10.798674+0.0001i |  | 0.010799+3.455576i | 0.116269+37.31564i | 10.809473+3.455676i | 1.011035+3.128907i | 1.011135-5.307557i |  | 25 | 5.5709 | 31.0345 | [8 empty] | 3.2 | 5.403
[13 empty] | kVLLsys (System Line-to-Line Voltage Rating): | 12.47 |  |  | kV | [10 empty] | Xeff Filter Effective Reactance): | 25.9168 |  |  | Ohms | [24 empty] | 3.4 | 0.0001-7.940201i | 0.000000001 | 0.010799+3.671549i | 10.798674+0.0001i |  | 0.010799+3.671549i | 0.116248+39.647862i | 10.809473+3.671649i | 1.126636+3.285197i | 1.126736-4.655004i |  | 29 | 0 | 0 | [8 empty] | 3.4 | 4.7894
|  |  | Qeff (3-Phase Output Rating of Filter): | [10 empty] | 6000 |  |  | kvar | [16 empty] | ICAP (Fundamental Current per Capacitor): | [8 empty] | 55.6248 |  |  | amps |  |  | Capacitive Reactance (per can): | 134.9834 | Ohms | [5 empty] | 3.6 | 0.0001-7.499079i | 0.000000001 | 0.010799+3.887523i | 10.798674+0.0001i |  | 0.010799+3.887523i | 0.116226+41.980095i | 10.809473+3.887623i | 1.246296+3.435409i | 1.246396-4.06367i |  | 31 | 0 | 0 | [8 empty] | 3.6 | 4.2505
|  |  | hn (Tuning Point of Filter): | [10 empty] | 5 |  |  | (harmonic number) | [10 empty] | hf : | 300 |  |  | Hz |  | I CAP FUSE (Minimum Fuse Rating): | [8 empty] | 100.1247 |  |  | amps |  |  | Capacitance (per can): | 19.6518 | µF | [5 empty] | 3.8 | 0.0001-7.104391i | 0.000000001 | 0.010799+4.103496i | 10.798674+0.0001i |  | 0.010799+4.103496i | 0.116205+44.312317i | 10.809473+4.103596i | 1.369616+3.57945i | 1.369716-3.524941i |  | 35 | 4.1208 | 16.9811 | [8 empty] | 3.8 | 3.7817
|  |  | f (System Frequency): | [10 empty] | 60 |  |  | (HZ) | [10 empty] | IRATED FUNDAMENTAL: | 278.1241 |  |  | amps |  | VCAP FUNDAMENTAL VOLTAGE: | [8 empty] | 7.5084 |  |  | kV | [10 empty] | 4 | 0.0001-6.749171i | 0.000000001 | 0.010799+4.319469i | 10.798674+0.0001i |  | 0.010799+4.319469i | 0.116183+46.644539i | 10.809473+4.319569i | 1.4962+3.717258i | 1.4963-3.031913i |  | 37 | 3.9136 | 15.3165 | [8 empty] | 4 | 3.381
| DF (Damping Factor of High-Pass Filter): | [12 empty] | 2 | [13 empty] | IFILTER RMS CURRENT: | 314.8858 |  |  | amps |  | VCAP RMS VOLTAGE: | [8 empty] | 7.536 |  |  | kV | [10 empty] | 4.2 | 0.0001-6.427782i | 0.000000001 | 0.010799+4.535443i | 10.798674+0.0001i |  | 0.010799+4.535443i | 0.116161+48.976771i | 10.809473+4.535543i | 1.625663+3.848801i | 1.625763-2.578981i |  |  |  | 452.5293 | [8 empty] | 4.2 | 3.0486
[34 empty] | VCAP, PEAK CAP VOLTAGE: | [8 empty] | 12.2311 |  |  | kV | [10 empty] | 4.4 | 0.0001-6.13561i | 0.000000001 | 0.010799+4.751416i | 10.798674+0.0001i |  | 0.010799+4.751416i | 0.11614+51.308994i | 10.809473+4.751516i | 1.757625+3.974071i | 1.757725-2.161539i | [12 empty] | 4.4 | 2.786
| Expected Harmonic Current (amps) Into Line Side of Filter of Filter Branch/Stage | [32 empty] | ICAP RMS CURRENT: | [8 empty] | 62.9772 |  |  | amps | [10 empty] | 4.6 | 0.0001-5.868844i | 0.000000001 | 0.010799+4.96739i | 10.798674+0.0001i |  | 0.010799+4.96739i | 0.116118+53.641226i | 10.809473+4.96749i | 1.89172+4.093088i | 1.89182-1.775756i | [12 empty] | 4.6 | 2.5947
| (n) Harmonic: | [5 empty] | 1 | 2 |  | 3 |  | 4 | 5 |  | 7 |  | 11 |  | 13 | 17 | 19 |  | 23 |  | 25 | 29 |  | 31 |  | 35 |  | 37 |  | QCAPACITOR (1-phase): | [8 empty] | 2178.8087 |  |  | kvar | [10 empty] | 4.8 | 0.0001-5.624309i | 0.000000001 | 0.010799+5.183363i | 10.798674+0.0001i |  | 0.010799+5.183363i | 0.116097+55.973448i | 10.809473+5.183463i | 2.027591+4.205894i | 2.027691-1.418415i | [12 empty] | 4.8 | 2.4746
| (In) Filter current: | [5 empty] | 278.1241 | 0 |  | 0 |  | 0 | 100 |  | 80 |  | 60 |  | 30 | 20 | 10 |  | 10 |  | 10 | 0 |  | 0 |  | 10 |  | 10 | [24 empty] | 5 | 0.0001-5.399337i | 0.000000001 | 0.010799+5.399337i | 10.798674+0.0001i |  | 0.010799+5.399337i | 0.116075+58.305681i | 10.809473+5.399437i | 2.164901+4.312554i | 2.165001-1.086783i | [12 empty] | 5 | 2.4225
[57 empty] | 5.2 | 0.0001-5.19167i | 0.000000001 | 0.010799+5.61531i | 10.798674+0.0001i |  | 0.010799+5.61531i | 0.116053+60.637903i | 10.809473+5.61541i | 2.303321+4.413148i | 2.303421-0.778522i | [12 empty] | 5.2 | 2.4314
| Capacitor Rating Details | [55 empty] | 5.4 | 0.0001-4.999386i | 0.000000001 | 0.010799+5.831284i | 10.798674+0.0001i |  | 0.010799+5.831284i | 0.116032+62.970136i | 10.809473+5.831384i | 2.442545+4.507779i | 2.442645-0.491607i | [12 empty] | 5.4 | 2.4916
VCAP RATING (Voltage Rating of Capacitor): | [13 empty] | 9.96 |  |  | kV | [9 empty] | Individual Capacitor Rating: | 734.9169 |  |  | kvar | [25 empty] | 5.6 | 0.0001-4.820836i | 0.000000001 | 0.010799+6.047257i | 10.798674+0.0001i |  | 0.010799+6.047257i | 0.11601+65.302358i | 10.809473+6.047357i | 2.582277+4.596561i | 2.582377-0.224275i | [12 empty] | 5.6 | 2.5921
N (Number of Capacitors Per Phase): | [13 empty] | 5 | [12 empty] | Q RATED PER PHASE: | 3674.5846 |  |  | kvar | [25 empty] | 5.8 | 0.0001-4.654601i | 0.000000001 | 0.010799+6.263231i | 10.798674+0.0001i |  | 0.010799+6.263231i | 0.115989+67.634591i | 10.809473+6.263331i | 2.722244+4.679624i | 2.722344+0.025023i | [12 empty] | 5.8 | 2.7225
[7 empty] | HD- Heavy Duty Capacitors | [19 empty] | XC: | 26.9967 |  |  | Ohms | [25 empty] | 6 | 0.0001-4.499447i | 0.000000001 | 0.010799+6.479204i | 10.798674+0.0001i |  | 0.010799+6.479204i | 0.115967+69.966813i | 10.809473+6.479304i | 2.862186+4.757109i | 2.862286+0.257662i | [12 empty] | 6 | 2.8739
[27 empty] | Capacitor Capacitance (per phase): | 98.26 |  |  | 𝜇F/Phase | [25 empty] | 6.2 | 0.0001-4.354304i | 0.000000001 | 0.010799+6.695178i | 10.798674+0.0001i |  | 0.010799+6.695178i | 0.115945+72.299046i | 10.809473+6.695278i | 3.001863+4.829166i | 3.001963+0.474862i | [12 empty] | 6.2 | 3.0393
[57 empty] | 6.4 | 0.0001-4.218232i | 0.000000001 | 0.010799+6.911151i | 10.798674+0.0001i |  | 0.010799+6.911151i | 0.115924+74.631268i | 10.809473+6.911251i | 3.14105+4.895954i | 3.14115+0.677722i | [12 empty] | 6.4 | 3.2134
| Tuning Reactor | [55 empty] | 6.6 | 0.0001-4.090407i | 0.000000001 | 0.010799+7.127125i | 10.798674+0.0001i |  | 0.010799+7.127125i | 0.115902+76.963501i | 10.809473+7.127225i | 3.279541+4.95764i | 3.279641+0.867233i | [12 empty] | 6.6 | 3.3924
| X/Rratio (Tuning Reactor at System Frequency): | [12 empty] | 100 |  |  |  | XL (Inductive Reactance): | [9 empty] | 1.0799 |  |  | ohms | [25 empty] | 6.8 | 0.0001-3.970101i | 0.000000001 | 0.010799+7.343098i | 10.798674+0.0001i |  | 0.010799+7.343098i | 0.115881+79.295723i | 10.809473+7.343198i | 3.417147+5.014392i | 3.417247+1.044291i | [12 empty] | 6.8 | 3.5733
[13 empty] | Enter Fundamental Current Design Margin: | 1.5 |  |  | HL (Inductance): | [10 empty] | 2.8645 |  |  | mH | [25 empty] | 7 | 0.0001-3.856669i | 0.000000001 | 0.010799+7.559072i | 10.798674+0.0001i |  | 0.010799+7.559072i | 0.115859+81.627955i | 10.809473+7.559172i | 3.553693+5.066387i | 3.553793+1.209718i | [12 empty] | 7 | 3.754
[13 empty] | Enter Harmonic Current Design Margin: | 1.5 | [42 empty] | 7.2 | 0.0001-3.749539i | 0.000000001 | 0.010799+7.775045i | 10.798674+0.0001i |  | 0.010799+7.775045i | 0.115837+83.960177i | 10.809473+7.775145i | 3.689022+5.113801i | 3.689122+1.364262i | [12 empty] | 7.2 | 3.9333
[57 empty] | 7.4 | 0.0001-3.648201i | 0.000000001 | 0.010799+7.991018i | 10.798674+0.0001i |  | 0.010799+7.991018i | 0.115816+86.292399i | 10.809473+7.991118i | 3.822991+5.156813i | 3.823091+1.508612i | [12 empty] | 7.4 | 4.11
| High-Pass Resistor | [55 empty] | 7.6 | 0.0001-3.552195i | 0.000000001 | 0.010799+8.206992i | 10.798674+0.0001i |  | 0.010799+8.206992i | 0.115794+88.624632i | 10.809473+8.207092i | 3.955472+5.195601i | 3.955572+1.643406i | [12 empty] | 7.6 | 4.2834
[13 empty] | Rw (Resistor KW/Phase - Specified): | 100 |  |  | kW/Phase | [39 empty] | 7.8 | 0.0001-3.461113i | 0.000000001 | 0.010799+8.422965i | 10.798674+0.0001i |  | 0.010799+8.422965i | 0.115773+90.956854i | 10.809473+8.423065i | 4.086351+5.230344i | 4.086451+1.769231i | [12 empty] | 7.8 | 4.453
[10 empty] | Ifundamental resistor current (actual): | 90.2135 |  | amps | [13 empty] | R (Resistor Ohm rating/phase): | 10.7987 |  |  | Ohms | [25 empty] | 8 | 0.0001-3.374586i | 0.000000001 | 0.010799+8.638939i | 10.798674+0.0001i |  | 0.010799+8.638939i | 0.115751+93.289087i | 10.809473+8.639039i | 4.215526+5.261218i | 4.215626+1.886632i | [12 empty] | 8 | 4.6185
[10 empty] | Ifundamental resistor current (specified): | 96.231 |  | amps | [13 empty] | (Rw) (Resistor KW/phase, actual): | 87.8847 |  |  | kW/Phase | [25 empty] | 8.2 | 0.0001-3.292279i | 0.000000001 | 0.010799+8.854912i | 10.798674+0.0001i |  | 0.010799+8.854912i | 0.115729+95.621309i | 10.809473+8.855012i | 4.342909+5.288398i | 4.343009+1.996119i | [12 empty] | 8.2 | 4.7798
[80 empty] | 8.4 | 4.9366
[80 empty] | 8.6 | 5.089
[57 empty] | 8.4 | 0.0001-3.213891i | 0.000000001 | 0.010799+9.070886i | 10.798674+0.0001i |  | 0.010799+9.070886i | 0.115708+97.953542i | 10.809473+9.070986i | 4.468423+5.312057i | 4.468523+2.098166i | [12 empty] | 8.8 | 5.2369
[57 empty] | 8.6 | 0.0001-3.139149i | 0.000000001 | 0.010799+9.286859i | 10.798674+0.0001i |  | 0.010799+9.286859i | 0.115686+100.285764i | 10.809473+9.286959i | 4.592002+5.332363i | 4.592102+2.193214i | [12 empty] | 9 | 5.3804
[57 empty] | 8.8 | 0.0001-3.067805i | 0.000000001 | 0.010799+9.502833i | 10.798674+0.0001i |  | 0.010799+9.502833i | 0.115665+102.617997i | 10.809473+9.502933i | 4.71359+5.349481i | 4.71369+2.281676i | [12 empty] | 9.2 | 5.5195
[80 empty] | 9.4 | 5.6544
|  | Info@VarStec.com | [30 empty] | Rev Date: 4-19-2026 |  | Info@VarStec.com | [16 empty] | 2 ¦ P a g e |  |  |  |  | 9 | 0.0001-2.999632i | 0.000000001 | 0.010799+9.718806i | 10.798674+0.0001i |  | 0.010799+9.718806i | 0.115643+104.950219i | 10.809473+9.718906i | 4.83314+5.363572i | 4.83324+2.36394i | [12 empty] | 9.6 | 5.785
[57 empty] | 9.2 | 0.0001-2.934422i | 0.000000001 | 0.010799+9.93478i | 10.798674+0.0001i |  | 0.010799+9.93478i | 0.115621+107.282452i | 10.809473+9.93488i | 4.950616+5.374793i | 4.950716+2.440371i | [12 empty] | 9.8 | 5.9116
[57 empty] | 9.4 | 0.0001-2.871988i | 0.000000001 | 0.010799+10.150753i | 10.798674+0.0001i |  | 0.010799+10.150753i | 0.1156+109.614674i | 10.809473+10.150853i | 5.065986+5.383296i | 5.066086+2.511308i | [12 empty] | 10 | 6.0343
[57 empty] | 9.6 | 0.0001-2.812155i | 0.000000001 | 0.010799+10.366727i | 10.798674+0.0001i |  | 0.010799+10.366727i | 0.115578+111.946906i | 10.809473+10.366827i | 5.179232+5.389227i | 5.179332+2.577072i | [12 empty] | 10.2 | 6.1531
[57 empty] | 9.8 | 0.0001-2.754764i | 0.000000001 | 0.010799+10.5827i | 10.798674+0.0001i |  | 0.010799+10.5827i | 0.115557+114.279128i | 10.809473+10.5828i | 5.290335+5.39273i | 5.290435+2.637966i | [12 empty] | 10.4 | 6.2681
[57 empty] | 10 | 0.0001-2.699668i | 0.000000001 | 0.010799+10.798674i | 10.798674+0.0001i |  | 0.010799+10.798674i | 0.115535+116.611361i | 10.809473+10.798774i | 5.39929+5.39394i | 5.39939+2.694272i | [12 empty] | 10.6 | 6.3795
| Enter Customer PO # ¦ Stage 1 | [32 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 10.2 | 0.0001-2.646734i | 0.000000001 | 0.010799+11.014647i | 10.798674+0.0001i |  | 0.010799+11.014647i | 0.115513+118.943583i | 10.809473+11.014747i | 5.506091+5.392991i | 5.506191+2.746257i | [12 empty] | 10.8 | 6.4874
[57 empty] | 10.4 | 0.0001-2.595835i | 0.000000001 | 0.010799+11.230621i | 10.798674+0.0001i |  | 0.010799+11.230621i | 0.115492+121.275816i | 10.809473+11.230721i | 5.610742+5.390007i | 5.610842+2.794172i | [12 empty] | 11 | 6.5919
| Table of Currents and Voltages | [32 empty] | 📐 SIMPLIFIED ONE-LINE DIAGRAM | [18 empty] | (In) Filter Current | (In) Filter Current | Calculated Reactor Current | VarStec Reactor Rating | 10.6 | 0.0001-2.546857i | 0.000000001 | 0.010799+11.446594i | 10.798674+0.0001i |  | 0.010799+11.446594i | 0.11547+123.608038i | 10.809473+11.446694i | 5.713249+5.385113i | 5.713349+2.838256i | [12 empty] | 11.2 | 6.6932
[16 empty] | IREACTOR CURRENT (amps) | [40 empty] | 10.8 | 0.0001-2.499693i | 0.000000001 | 0.010799+11.662568i | 10.798674+0.0001i |  | 0.010799+11.662568i | 0.115449+125.940271i | 10.809473+11.662668i | 5.813623+5.378422i | 5.813723+2.878729i | [12 empty] | 11.4 | 6.7912
[6 empty] | (In) Filter Current (amps): |  |  |  |  | VCAP Voltage (volts) | [22 empty] | 12.47kV, 60Hz High-Pass Filter, Wye-Connected | [22 empty] | 11 | 0.0001-2.454244i | 0.000000001 | 0.010799+11.878541i | 10.798674+0.0001i |  | 0.010799+11.878541i | 0.115427+128.272493i | 10.809473+11.878641i | 5.91188+5.370049i | 5.91198+2.915805i | [12 empty] | 11.6 | 6.8862
| Harmonic #: (n) | [19 empty] | IRESISTOR CURRENT (amps) | [5 empty] | Voltage Distortion* | [6 empty] | 6,000 Kvar 3-Phase, 5.0 Tuning | [22 empty] | 11.2 | 0.0001-2.410418i | 0.000000001 | 0.010799+12.094514i | 10.798674+0.0001i |  | 0.010799+12.094514i | 0.115405+130.604715i | 10.809473+12.094614i | 6.008037+5.360097i | 6.008137+2.949679i | [12 empty] | 11.8 | 6.9783
[53 empty] | 1 | 278.1241 | 276.7439 | 415.1158 | 11.4 | 0.0001-2.36813i | 0.000000001 | 0.010799+12.310488i | 10.798674+0.0001i |  | 0.010799+12.310488i | 0.115384+132.936948i | 10.809473+12.310588i | 6.102116+5.34867i | 6.102216+2.98054i | [12 empty] | 12 | 7.0675
| 1 |  |  |  |  | 278.1241 |  |  |  |  | 7508.4297 |  |  |  |  | 276.7439 |  |  |  |  | 27.6744 | [5 empty] | 100.2% | [16 empty] | Fundamental amps 278.1 amps/phase | [8 empty] | 2 | 0 | 0 | 0 | 11.6 | 0.0001-2.3273i | 0.000000001 | 0.010799+12.526461i | 10.798674+0.0001i |  | 0.010799+12.526461i | 0.115362+135.26917i | 10.809473+12.526561i | 6.194141+5.335865i | 6.194241+3.008565i | [12 empty] | 12.2 | 7.1539
| 2 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0% | [16 empty] | RMS Current 314.89 amps/phase | [8 empty] | 3 | 0 | 0 | 0 | 11.8 | 0.0001-2.287855i | 0.000000001 | 0.010799+12.742435i | 10.798674+0.0001i |  | 0.010799+12.742435i | 0.115341+137.601403i | 10.809473+12.742535i | 6.284138+5.321773i | 6.284238+3.033918i | [12 empty] | 12.4 | 7.2377
| 3 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0% | [25 empty] | 4 | 0 | 0 | 0 | 12 | 0.0001-2.249724i | 0.000000001 | 0.010799+12.958408i | 10.798674+0.0001i |  | 0.010799+12.958408i | 0.115319+139.933625i | 10.809473+12.958508i | 6.372134+5.306482i | 6.372234+3.056758i | [12 empty] | 12.6 | 7.3189
| 4 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0% | [16 empty] | Reactor: 1.08 ohms, 2.86 mH | [8 empty] | 5 | 100 | 89.4427 | 134.1641 | 12.2 | 0.0001-2.212843i | 0.000000001 | 0.010799+13.174382i | 10.798674+0.0001i |  | 0.010799+13.174382i | 0.115297+142.265857i | 10.809473+13.174482i | 6.458161+5.290076i | 6.458261+3.077233i | [12 empty] | 12.8 | 7.3977
| 5 |  |  |  |  | 100 |  |  |  |  | 539.9337 |  |  |  |  | 89.4427 |  |  |  |  | 44.7214 | [5 empty] | 3.365% | [12 empty] | High-Pass Resistor: 10.8 ohms/Phase |  |  |  | I1= 276.7 amps nominal | [8 empty] | 7 | 80 | 65.5386 | 98.3078 | 12.4 | 0.0001-2.177152i | 0.000000001 | 0.010799+13.390355i | 10.798674+0.0001i |  | 0.010799+13.390355i | 0.115276+144.598079i | 10.809473+13.390455i | 6.542248+5.272635i | 6.542348+3.095483i | [12 empty] | 13 | 7.474
| 7 |  |  |  |  | 80 |  |  |  |  | 308.5335 |  |  |  |  | 65.5386 |  |  |  |  | 45.877 | [5 empty] | 4.171% | [12 empty] | 88 KW/Phase Total | [12 empty] | 11 | 60 | 40.3604 | 60.5406 | 12.6 | 0.0001-2.142594i | 0.000000001 | 0.010799+13.606329i | 10.798674+0.0001i |  | 0.010799+13.606329i | 0.115254+146.930312i | 10.809473+13.606429i | 6.62443+5.254232i | 6.62453+3.111638i | [12 empty] | 13.2 | 7.5481
| 11 |  |  |  |  | 60 |  |  |  |  | 147.2546 |  |  |  |  | 40.3604 |  |  |  |  | 44.3964 | [5 empty] | 5.494% | [12 empty] | 90.2 RMS Amps | [12 empty] | 13 | 30 | 18.2913 | 27.437 | 12.8 | 0.0001-2.109116i | 0.000000001 | 0.010799+13.822302i | 10.798674+0.0001i |  | 0.010799+13.822302i | 0.115233+149.262534i | 10.809473+13.822402i | 6.704738+5.234941i | 6.704838+3.125825i | [12 empty] | 13.4 | 7.6199
| 13 |  |  |  |  | 30 |  |  |  |  | 62.3 |  |  |  |  | 18.2913 |  |  |  |  | 23.7787 | [5 empty] | 3.114% | [25 empty] | 17 | 20 | 10.1404 | 15.2106 | 13 | 0.0001-2.076668i | 0.000000001 | 0.010799+14.038276i | 10.798674+0.0001i |  | 0.010799+14.038276i | 0.115211+151.594767i | 10.809473+14.038376i | 6.783209+5.214827i | 6.783309+3.138159i | [12 empty] | 13.6 | 7.6896
| 17 |  |  |  |  | 20 |  |  |  |  | 31.7608 |  |  |  |  | 10.1404 |  |  |  |  | 17.2387 | [5 empty] | 2.392% | [25 empty] | 19 | 10 | 4.6575 | 6.9862 | 13.2 | 0.0001-2.045203i | 0.000000001 | 0.010799+14.254249i | 10.798674+0.0001i |  | 0.010799+14.254249i | 0.115189+153.926989i | 10.809473+14.254349i | 6.859876+5.193956i | 6.859976+3.148753i | [12 empty] | 13.8 | 7.7573
| 19 |  |  |  |  | 10 |  |  |  |  | 14.2088 |  |  |  |  | 4.6575 |  |  |  |  | 8.8492 | [5 empty] | 1.247% | [16 empty] | Capacitor Fuse: 100 (Minimum Amps) | [8 empty] | 23 | 10 | 3.9873 | 5.9809 | 13.4 | 0.0001-2.014678i | 0.000000001 | 0.010799+14.470223i | 10.798674+0.0001i |  | 0.010799+14.470223i | 0.115168+156.259222i | 10.809473+14.470323i | 6.934776+5.172387i | 6.934876+3.157709i | [12 empty] | 14 | 7.8229
| 23 |  |  |  |  | 10 |  |  |  |  | 11.7377 |  |  |  |  | 3.9873 |  |  |  |  | 9.1707 | [5 empty] | 1.319% | [25 empty] | 25 | 10 | 3.7139 | 5.5709 | 13.6 | 0.0001-1.98505i | 0.000000001 | 0.010799+14.686196i | 10.798674+0.0001i |  | 0.010799+14.686196i | 0.115146+158.591444i | 10.809473+14.686296i | 7.007944+5.150178i | 7.008044+3.165128i | [12 empty] | 14.2 | 7.8866
| 25 |  |  |  |  | 10 |  |  |  |  | 10.7987 |  |  |  |  | 3.7139 |  |  |  |  | 9.2848 | [5 empty] | 1.344% | [25 empty] | 29 | 0 | 0 | 0 | 13.8 | 0.0001-1.956281i | 0.000000001 | 0.010799+14.90217i | 10.798674+0.0001i |  | 0.010799+14.90217i | 0.115125+160.923677i | 10.809473+14.90227i | 7.079416+5.127382i | 7.079516+3.171101i | [12 empty] | 14.4 | 7.9485
| 29 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0% | [16 empty] | Capacitor: Qty(15), 735 kvar, 9.96 kV, 19.65 µF/Can | [8 empty] | 31 | 0 | 0 | 0 | 14 | 0.0001-1.928335i | 0.000000001 | 0.010799+15.118143i | 10.798674+0.0001i |  | 0.010799+15.118143i | 0.115103+163.255899i | 10.809473+15.118243i | 7.149229+5.104052i | 7.149329+3.175717i | [12 empty] | 14.6 | 8.0086
| 31 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0% | [25 empty] | 35 | 10 | 2.7472 | 4.1208 | 14.2 | 0.0001-1.901175i | 0.000000001 | 0.010799+15.334117i | 10.798674+0.0001i |  | 0.010799+15.334117i | 0.115081+165.588132i | 10.809473+15.334217i | 7.217419+5.080235i | 7.217519+3.17906i | [12 empty] | 14.8 | 8.0669
| 35 |  |  |  |  | 10 |  |  |  |  | 7.7133 |  |  |  |  | 2.7472 |  |  |  |  | 9.6152 | [5 empty] | 1.416% | [25 empty] | 37 | 10 | 2.6091 | 3.9136 | 14.4 | 0.0001-1.87477i | 0.000000001 | 0.010799+15.55009i | 10.798674+0.0001i |  | 0.010799+15.55009i | 0.11506+167.920354i | 10.809473+15.55019i | 7.284022+5.055975i | 7.284122+3.181205i | [12 empty] | 15 | 8.1235
| 37 |  |  |  |  | 10 |  |  |  |  | 7.2964 |  |  |  |  | 2.6091 |  |  |  |  | 9.6536 | [5 empty] | 1.425% | [29 empty] | 14.6 | 0.0001-1.849088i | 0.000000001 | 0.010799+15.766063i | 10.798674+0.0001i |  | 0.010799+15.766063i | 0.115038+170.252576i | 10.809473+15.766163i | 7.349073+5.031317i | 7.349173+3.182229i | [12 empty] | 15.2 | 8.1786
[5 empty] | RMS | 314.8858 |  |  |  |  | 7535.9885 |  |  |  |  | 301.6862 |  |  |  |  | 90.2135 | [5 empty] | 9.136% | [29 empty] | 14.8 | 0.0001-1.8241i | 0.000000001 | 0.010799+15.982037i | 10.798674+0.0001i |  | 0.010799+15.982037i | 0.115017+172.584808i | 10.809473+15.982137i | 7.412609+5.006301i | 7.412709+3.182201i | [12 empty] | 15.4 | 8.2321
| * Voltage distortion at filter incoming based on specified harmonic currents in rows 24 and 25 of page 1. | [55 empty] | 15 | 0.0001-1.799779i | 0.000000001 | 0.010799+16.19801i | 10.798674+0.0001i |  | 0.010799+16.19801i | 0.114995+174.917031i | 10.809473+16.19811i | 7.474665+4.980963i | 7.474765+3.181184i | [12 empty] | 15.6 | 8.2841
[57 empty] | 15.2 | 0.0001-1.776098i | 0.000000001 | 0.010799+16.413984i | 10.798674+0.0001i |  | 0.010799+16.413984i | 0.114973+177.249263i | 10.809473+16.414084i | 7.535275+4.955341i | 7.535375+3.179243i | [12 empty] | 15.8 | 8.3346
[57 empty] | 15.4 | 0.0001-1.753031i | 0.000000001 | 0.010799+16.629957i | 10.798674+0.0001i |  | 0.010799+16.629957i | 0.114952+179.581485i | 10.809473+16.630057i | 7.594475+4.929467i | 7.594575+3.176436i | [12 empty] | 16 | 8.3837
[57 empty] | 15.6 | 0.0001-1.730557i | 0.000000001 | 0.010799+16.845931i | 10.798674+0.0001i |  | 0.010799+16.845931i | 0.11493+181.913718i | 10.809473+16.846031i | 7.652297+4.903373i | 7.652397+3.172816i | [12 empty] | 16.2 | 8.4315
[57 empty] | 15.8 | 0.0001-1.708651i | 0.000000001 | 0.010799+17.061904i | 10.798674+0.0001i |  | 0.010799+17.061904i | 0.114909+184.24594i | 10.809473+17.062004i | 7.708777+4.877089i | 7.708877+3.168438i | [12 empty] | 16.4 | 8.478
[57 empty] | 16 | 0.0001-1.687293i | 0.000000001 | 0.010799+17.277878i | 10.798674+0.0001i |  | 0.010799+17.277878i | 0.114887+186.578173i | 10.809473+17.277978i | 7.763946+4.850642i | 7.764046+3.163349i | [12 empty] | 16.6 | 8.5232
[57 empty] | 16.2 | 0.0001-1.666462i | 0.000000001 | 0.010799+17.493851i | 10.798674+0.0001i |  | 0.010799+17.493851i | 0.114865+188.910395i | 10.809473+17.493951i | 7.817838+4.824058i | 7.817938+3.157596i | [12 empty] | 16.8 | 8.5672
[57 empty] | 16.4 | 0.0001-1.646139i | 0.000000001 | 0.010799+17.709825i | 10.798674+0.0001i |  | 0.010799+17.709825i | 0.114844+191.242628i | 10.809473+17.709925i | 7.870483+4.797363i | 7.870583+3.151224i | [12 empty] | 17 | 8.61
[57 empty] | 16.6 | 0.0001-1.626306i | 0.000000001 | 0.010799+17.925798i | 10.798674+0.0001i |  | 0.010799+17.925798i | 0.114822+193.57485i | 10.809473+17.925898i | 7.921914+4.770578i | 7.922014+3.144272i | [12 empty] | 17.2 | 8.6516
[57 empty] | 16.8 | 0.0001-1.606945i | 0.000000001 | 0.010799+18.141772i | 10.798674+0.0001i |  | 0.010799+18.141772i | 0.114801+195.907083i | 10.809473+18.141872i | 7.97216+4.743725i | 7.97226+3.13678i | [12 empty] | 17.4 | 8.6922
[57 empty] | 17 | 0.0001-1.58804i | 0.000000001 | 0.010799+18.357745i | 10.798674+0.0001i |  | 0.010799+18.357745i | 0.114779+198.239305i | 10.809473+18.357845i | 8.021253+4.716825i | 8.021353+3.128785i | [12 empty] | 17.6 | 8.7316
[57 empty] | 17.2 | 0.0001-1.569575i | 0.000000001 | 0.010799+18.573719i | 10.798674+0.0001i |  | 0.010799+18.573719i | 0.114758+200.571538i | 10.809473+18.573819i | 8.069221+4.689895i | 8.069321+3.12032i | [12 empty] | 17.8 | 8.7701
[57 empty] | 17.4 | 0.0001-1.551534i | 0.000000001 | 0.010799+18.789692i | 10.798674+0.0001i |  | 0.010799+18.789692i | 0.114736+202.90376i | 10.809473+18.789792i | 8.116092+4.662954i | 8.116192+3.11142i | [12 empty] | 18 | 8.8075
[57 empty] | 17.6 | 0.0001-1.533903i | 0.000000001 | 0.010799+19.005666i | 10.798674+0.0001i |  | 0.010799+19.005666i | 0.114714+205.235992i | 10.809473+19.005766i | 8.161896+4.636018i | 8.161996+3.102115i | [12 empty] | 18.2 | 8.844
[57 empty] | 17.8 | 0.0001-1.516668i | 0.000000001 | 0.010799+19.221639i | 10.798674+0.0001i |  | 0.010799+19.221639i | 0.114693+207.568214i | 10.809473+19.221739i | 8.206658+4.609102i | 8.206758+3.092434i | [12 empty] | 18.4 | 8.8795
[57 empty] | 18 | 0.0001-1.499816i | 0.000000001 | 0.010799+19.437613i | 10.798674+0.0001i |  | 0.010799+19.437613i | 0.114671+209.900447i | 10.809473+19.437713i | 8.250408+4.582221i | 8.250508+3.082405i | [12 empty] | 18.6 | 8.9141
[57 empty] | 18.2 | 0.0001-1.483334i | 0.000000001 | 0.010799+19.653586i | 10.798674+0.0001i |  | 0.010799+19.653586i | 0.11465+212.232669i | 10.809473+19.653686i | 8.293169+4.555387i | 8.293269+3.072053i | [12 empty] | 18.8 | 8.9479
[57 empty] | 18.4 | 0.0001-1.467211i | 0.000000001 | 0.010799+19.869559i | 10.798674+0.0001i |  | 0.010799+19.869559i | 0.114628+214.564891i | 10.809473+19.869659i | 8.334968+4.528612i | 8.335068+3.061401i | [12 empty] | 19 | 8.9808
[57 empty] | 18.6 | 0.0001-1.451435i | 0.000000001 | 0.010799+20.085533i | 10.798674+0.0001i |  | 0.010799+20.085533i | 0.114606+216.897124i | 10.809473+20.085633i | 8.37583+4.50191i | 8.37593+3.050475i | [12 empty] | 19.2 | 9.0128
|  | Info@VarStec.com | [30 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 4 ¦ P a g e |  |  |  |  | 18.8 | 0.0001-1.435994i | 0.000000001 | 0.010799+20.301506i | 10.798674+0.0001i |  | 0.010799+20.301506i | 0.114585+219.229346i | 10.809473+20.301606i | 8.415779+4.475289i | 8.415879+3.039295i | [12 empty] | 19.4 | 9.0441
[57 empty] | 19 | 0.0001-1.420878i | 0.000000001 | 0.010799+20.51748i | 10.798674+0.0001i |  | 0.010799+20.51748i | 0.114563+221.561579i | 10.809473+20.51758i | 8.454839+4.44876i | 8.454939+3.027882i | [12 empty] | 19.6 | 9.0746
[57 empty] | 19.2 | 0.0001-1.406077i | 0.000000001 | 0.010799+20.733453i | 10.798674+0.0001i |  | 0.010799+20.733453i | 0.114542+223.893801i | 10.809473+20.733553i | 8.493032+4.422332i | 8.493132+3.016255i | [12 empty] | 19.8 | 9.1043
[57 empty] | 19.4 | 0.0001-1.391582i | 0.000000001 | 0.010799+20.949427i | 10.798674+0.0001i |  | 0.010799+20.949427i | 0.11452+226.226034i | 10.809473+20.949527i | 8.530381+4.396013i | 8.530481+3.004431i | [12 empty] | 20 | 9.1334
[57 empty] | 19.6 | 0.0001-1.377382i | 0.000000001 | 0.010799+21.1654i | 10.798674+0.0001i |  | 0.010799+21.1654i | 0.114498+228.558256i | 10.809473+21.1655i | 8.566908+4.369812i | 8.567008+2.99243i | [12 empty] | 20.2 | 9.1617
[57 empty] | 19.8 | 0.0001-1.363469i | 0.000000001 | 0.010799+21.381374i | 10.798674+0.0001i |  | 0.010799+21.381374i | 0.114477+230.890489i | 10.809473+21.381474i | 8.602634+4.343735i | 8.602734+2.980266i | [12 empty] | 20.4 | 9.1893
| Enter Customer PO # ¦ Stage 1 | [32 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 20 | 0.0001-1.349834i | 0.000000001 | 0.010799+21.597347i | 10.798674+0.0001i |  | 0.010799+21.597347i | 0.114455+233.222711i | 10.809473+21.597447i | 8.63758+4.31779i | 8.63768+2.967956i | [12 empty] | 20.6 | 9.2163
[57 empty] | 20.2 | 0.0001-1.33647i | 0.000000001 | 0.010799+21.813321i | 10.798674+0.0001i |  | 0.010799+21.813321i | 0.114434+235.554943i | 10.809473+21.813421i | 8.671766+4.291981i | 8.671866+2.955511i | [12 empty] | 20.8 | 9.2426
| 🧮 VENDOR SPECIFICATIONS | [32 empty] | 🧮 3-PHASE LOSS ESTIMATES | [22 empty] | 20.4 | 0.0001-1.323367i | 0.000000001 | 0.010799+22.029294i | 10.798674+0.0001i |  | 0.010799+22.029294i | 0.114412+237.887165i | 10.809473+22.029394i | 8.705212+4.266315i | 8.705312+2.942948i | [12 empty] | 21 | 9.2683
|  | Reactor Specification | [54 empty] | 20.6 | 0.0001-1.310519i | 0.000000001 | 0.010799+22.245268i | 10.798674+0.0001i |  | 0.010799+22.245268i | 0.11439+240.219398i | 10.809473+22.245368i | 8.737937+4.240797i | 8.738037+2.930278i | [12 empty] | 21.2 | 9.2934
[34 empty] | 60 Hertz Losses | [22 empty] | 20.8 | 0.0001-1.297918i | 0.000000001 | 0.010799+22.461241i | 10.798674+0.0001i |  | 0.010799+22.461241i | 0.114369+242.55162i | 10.809473+22.461341i | 8.769958+4.215432i | 8.770058+2.917514i | [12 empty] | 21.4 | 9.3179
|  |  |  | Filter Type: | High-Pass | [12 empty] | Return Quote to: | VarStec Power Solutions | [15 empty] | Capacitor Losses: | [6 empty] | 1102.3754 |  |  | Watts, 3-Phase or 3761 BTUs/Hour | [11 empty] | 21 | 0.0001-1.285556i | 0.000000001 | 0.010799+22.677215i | 10.798674+0.0001i |  | 0.010799+22.677215i | 0.114347+244.883853i | 10.809473+22.677315i | 8.801295+4.190223i | 8.801395+2.904667i | [12 empty] | 21.6 | 9.3419
|  |  |  | Stage/Branch: | Stage 1 | [29 empty] | Capacitor Fuse Losses: | [6 empty] | 3033.5537 |  |  | Watts, 3-Phase or 10351 BTUs/Hour | [11 empty] | 21.2 | 0.0001-1.273428i | 0.000000001 | 0.010799+22.893188i | 10.798674+0.0001i |  | 0.010799+22.893188i | 0.114326+247.216075i | 10.809473+22.893288i | 8.831965+4.165176i | 8.832065+2.891748i | [12 empty] | 21.8 | 9.3653
|  |  |  | Tuning Point: | 5 | [29 empty] | High-Pass Resistor Losses, 60 Hertz: | [6 empty] | 24811.1951 |  |  | Watts, 3-Phase or 84659 BTUs/Hour | [11 empty] | 21.4 | 0.0001-1.261527i | 0.000000001 | 0.010799+23.109162i | 10.798674+0.0001i |  | 0.010799+23.109162i | 0.114304+249.548308i | 10.809473+23.109262i | 8.861985+4.140292i | 8.862085+2.878765i | [12 empty] | 22 | 9.3881
[35 empty] | Iron-Core Reactor Losses, 60 Hertz: | [6 empty] | 2481.1195 |  |  | Watts, 3-Phase or 8466 BTUs/Hour | [11 empty] | 21.6 | 0.0001-1.249846i | 0.000000001 | 0.010799+23.325135i | 10.798674+0.0001i |  | 0.010799+23.325135i | 0.114282+251.88053i | 10.809473+23.325235i | 8.891372+4.115575i | 8.891472+2.865729i | [12 empty] | 22.2 | 9.4105
|  | Current Spectrum | [6 empty] | Tuning Reactor Details | [25 empty] | Total 60 Hz Losses: | [6 empty] | 31428.2437 |  |  | Watts, 3-Phase or 107238 BTUs/Hour | [11 empty] | 21.8 | 0.0001-1.23838i | 0.000000001 | 0.010799+23.541108i | 10.798674+0.0001i |  | 0.010799+23.541108i | 0.114261+254.212752i | 10.809473+23.541208i | 8.920141+4.091029i | 8.920241+2.852649i | [12 empty] | 22.4 | 9.4323
|  | Harm # |  |  | Amps | [11 empty] | Quantity: | 3 | [38 empty] | 22 | 0.0001-1.227122i | 0.000000001 | 0.010799+23.757082i | 10.798674+0.0001i |  | 0.010799+23.757082i | 0.114239+256.544985i | 10.809473+23.757182i | 8.948308+4.066655i | 8.948408+2.839533i | [12 empty] | 22.6 | 9.4536
|  | 1 |  |  | 415.1158 | [11 empty] | Number of Phases: | 1 | [16 empty] | Harmonic Losses Based on Specified Harmonics | [21 empty] | 22.2 | 0.0001-1.216067i | 0.000000001 | 0.010799+23.973055i | 10.798674+0.0001i |  | 0.010799+23.973055i | 0.114218+258.877207i | 10.809473+23.973155i | 8.97589+4.042456i | 8.97599+2.826389i | [12 empty] | 22.8 | 9.4745
|  | 2 |  |  | 0 | [11 empty] | System Voltage: | 12.47 |  | kV | [14 empty] | High-Pass Resistor Losses: | [6 empty] | 238842.9228 |  |  | Watts, 3-Phase or 814966 BTUs/Hour | [11 empty] | 22.4 | 0.0001-1.205209i | 0.000000001 | 0.010799+24.189029i | 10.798674+0.0001i |  | 0.010799+24.189029i | 0.114196+261.20944i | 10.809473+24.189129i | 9.002899+4.018433i | 9.002999+2.813224i | [12 empty] | 23 | 9.4949
|  | 3 |  |  | 0 | [11 empty] | BIL Rating: | 95 |  | kV | [14 empty] | Iron-Core Reactor Losses: | [6 empty] | 467.3903 |  |  | Watts, 3-Phase or 1595 BTUs/Hour | [11 empty] | 22.6 | 0.0001-1.194544i | 0.000000001 | 0.010799+24.405002i | 10.798674+0.0001i |  | 0.010799+24.405002i | 0.114174+263.541662i | 10.809473+24.405102i | 9.029352+3.994589i | 9.029452+2.800045i | [12 empty] | 23.2 | 9.5149
|  | 4 |  |  | 0 | [11 empty] | 60 Second Withstand Voltage: | 35 |  | kV | [14 empty] | Total Harmonic Losses: | [6 empty] | 239310.3132 |  |  | Watts, 3-Phase or 816561 BTUs/Hour | [11 empty] | 22.8 | 0.0001-1.184065i | 0.000000001 | 0.010799+24.620976i | 10.798674+0.0001i |  | 0.010799+24.620976i | 0.114153+265.873894i | 10.809473+24.621076i | 9.055262+3.970925i | 9.055362+2.78686i | [12 empty] | 23.4 | 9.5344
|  | 5 |  |  | 134.1641 | [11 empty] | Fundamental Frequency: | 60 |  | Hz | [36 empty] | 23 | 0.0001-1.173769i | 0.000000001 | 0.010799+24.836949i | 10.798674+0.0001i |  | 0.010799+24.836949i | 0.114131+268.206116i | 10.809473+24.837049i | 9.080642+3.947442i | 9.080742+2.773673i | [12 empty] | 23.6 | 9.5534
|  | 7 |  |  | 98.3078 | [11 empty] | Inductance: | 2.8645 |  | mH | [14 empty] | Total Losses - All: | [6 empty] | 270738.5569 |  |  | Watts, 3-Phase or 923798 BTUs/Hour | [11 empty] | 23.2 | 0.0001-1.16365i | 0.000000001 | 0.010799+25.052923i | 10.798674+0.0001i |  | 0.010799+25.052923i | 0.11411+270.538349i | 10.809473+25.053023i | 9.105506+3.924142i | 9.105606+2.760492i | [12 empty] | 23.8 | 9.5721
|  | 11 |  |  | 60.5406 | [11 empty] | Reactance at 60Hz: | 1.0799 |  | Ohms | [36 empty] | 23.4 | 0.0001-1.153704i | 0.000000001 | 0.010799+25.268896i | 10.798674+0.0001i |  | 0.010799+25.268896i | 0.114088+272.870571i | 10.809473+25.268996i | 9.129866+3.901024i | 9.129966+2.74732i | [12 empty] | 24 | 9.5904
|  | 13 |  |  | 27.437 | [11 empty] | Taps: | None | [38 empty] | 23.6 | 0.0001-1.143927i | 0.000000001 | 0.010799+25.48487i | 10.798674+0.0001i |  | 0.010799+25.48487i | 0.114066+275.202804i | 10.809473+25.48497i | 9.153736+3.87809i | 9.153836+2.734163i | [12 empty] | 24.2 | 9.6083
|  | 17 |  |  | 15.2106 | [11 empty] | Insulation Type: | Nomex | [38 empty] | 23.8 | 0.0001-1.134314i | 0.000000001 | 0.010799+25.700843i | 10.798674+0.0001i |  | 0.010799+25.700843i | 0.114045+277.535026i | 10.809473+25.700943i | 9.177128+3.85534i | 9.177228+2.721026i | [12 empty] | 24.4 | 9.6258
|  | 19 |  |  | 6.9862 | [11 empty] | Ambient: | 60C | [15 empty] | 🧮 HARMONIC FILTER DESIGN METHODOLOGY | [22 empty] | 24 | 0.0001-1.124862i | 0.000000001 | 0.010799+25.916817i | 10.798674+0.0001i |  | 0.010799+25.916817i | 0.114023+279.867259i | 10.809473+25.916917i | 9.200052+3.832774i | 9.200152+2.707912i | [12 empty] | 24.6 | 9.6429
|  | 23 |  |  | 5.9809 | [11 empty] | Temperature Rise: | 115C Rise over Ambient | [38 empty] | 24.2 | 0.0001-1.115565i | 0.000000001 | 0.010799+26.13279i | 10.798674+0.0001i |  | 0.010799+26.13279i | 0.114002+282.199481i | 10.809473+26.13289i | 9.222521+3.810393i | 9.222621+2.694828i | [12 empty] | 24.8 | 9.6597
|  | 25 |  |  | 5.5709 | [11 empty] | Winding Type: | CU/AL - Based On Price | [38 empty] | 24.4 | 0.0001-1.106421i | 0.000000001 | 0.010799+26.348764i | 10.798674+0.0001i |  | 0.010799+26.348764i | 0.11398+284.531714i | 10.809473+26.348864i | 9.244546+3.788197i | 9.244646+2.681776i | [12 empty] | 25 | 9.6761
|  | 29 |  |  | 0 | [11 empty] | Tack Winding to Core: | Yes | [38 empty] | 24.6 | 0.0001-1.097426i | 0.000000001 | 0.010799+26.564737i | 10.798674+0.0001i |  | 0.010799+26.564737i | 0.113958+286.863936i | 10.809473+26.564837i | 9.266138+3.766186i | 9.266238+2.66876i | [12 empty] | 25.2 | 9.6922
|  | 31 |  |  | 0 | [11 empty] | Enclosure: | None/Open Construction | [38 empty] | 24.8 | 0.0001-1.088576i | 0.000000001 | 0.010799+26.780711i | 10.798674+0.0001i |  | 0.010799+26.780711i | 0.113937+289.196169i | 10.809473+26.780811i | 9.287307+3.744359i | 9.287407+2.655783i | [12 empty] | 25.4 | 9.7079
|  | 35 |  |  | 4.1208 | [51 empty] | 25 | 0.0001-1.079867i | 0.000000001 | 0.010799+26.996684i | 10.798674+0.0001i |  | 0.010799+26.996684i | 0.113915+291.528391i | 10.809473+26.996784i | 9.308064+3.722716i | 9.308164+2.642849i | [12 empty] | 25.6 | 9.7233
|  | 37 |  |  | 3.9136 | [51 empty] | 25.2 | 0.0001-1.071297i | 0.000000001 | 0.010799+27.212658i | 10.798674+0.0001i |  | 0.010799+27.212658i | 0.113894+293.860623i | 10.809473+27.212758i | 9.328418+3.701256i | 9.328518+2.629959i | [12 empty] | 25.8 | 9.7384
|  | RMS: |  |  | 452.5293 | [51 empty] | 25.4 | 0.0001-1.062862i | 0.000000001 | 0.010799+27.428631i | 10.798674+0.0001i |  | 0.010799+27.428631i | 0.113872+296.192846i | 10.809473+27.428731i | 9.34838+3.67998i | 9.34848+2.617118i | [12 empty] | 26 | 9.7532
| Capacitor Specification | [55 empty] | 25.6 | 0.0001-1.054558i | 0.000000001 | 0.010799+27.644604i | 10.798674+0.0001i |  | 0.010799+27.644604i | 0.11385+298.525068i | 10.809473+27.644704i | 9.367958+3.658887i | 9.368058+2.604329i | [12 empty] | 26.2 | 9.7677
| A quantity of 15, 735 kvar, 95 kV BIL, 60 Hertz, all-film, low-loss, double-bushing capacitors designed, manufactured, and tested to applicable IEEE/ANSI and IEC standards, supplied by Cooper, GE, or Hitachi (no others), are required. The capacitors shall be connected unground-wye and shall have applicable over-voltage and blown-fuse protection. | [55 empty] | 25.8 | 0.0001-1.046383i | 0.000000001 | 0.010799+27.860578i | 10.798674+0.0001i |  | 0.010799+27.860578i | 0.113829+300.8573i | 10.809473+27.860678i | 9.387162+3.637975i | 9.387262+2.591592i | [12 empty] | 26.4 | 9.7819
[57 empty] | 26 | 0.0001-1.038334i | 0.000000001 | 0.010799+28.076551i | 10.798674+0.0001i |  | 0.010799+28.076551i | 0.113807+303.189522i | 10.809473+28.076651i | 9.406001+3.617244i | 9.406101+2.57891i | [12 empty] | 26.6 | 9.7959
[57 empty] | 26.2 | 0.0001-1.030408i | 0.000000001 | 0.010799+28.292525i | 10.798674+0.0001i |  | 0.010799+28.292525i | 0.113786+305.521755i | 10.809473+28.292625i | 9.424484+3.596694i | 9.424584+2.566286i | [12 empty] | 26.8 | 9.8095
[57 empty] | 26.4 | 0.0001-1.022602i | 0.000000001 | 0.010799+28.508498i | 10.798674+0.0001i |  | 0.010799+28.508498i | 0.113764+307.853977i | 10.809473+28.508598i | 9.442618+3.576323i | 9.442718+2.553721i | [12 empty] | 27 | 9.8229
| High-Pass Resistor specification | [55 empty] | 26.6 | 0.0001-1.014913i | 0.000000001 | 0.010799+28.724472i | 10.798674+0.0001i |  | 0.010799+28.724472i | 0.113742+310.18621i | 10.809473+28.724572i | 9.460413+3.556131i | 9.460513+2.541218i | [12 empty] | 27.2 | 9.836
| A quantity of 3 stainless steel grid resistors shall be provided. Each resistor shall have an ohmic value per phase of 10.8 ohms, a continuous power rating of 100 kW, and an RMS current rating of 96.23 amps. The resistor element shall be divided into 2 series groups to ensure adequate withstand voltage during switching transients, with the overall BIL rating coordinated to 95 kV. | [55 empty] | 26.8 | 0.0001-1.007339i | 0.000000001 | 0.010799+28.940445i | 10.798674+0.0001i |  | 0.010799+28.940445i | 0.113721+312.518432i | 10.809473+28.940545i | 9.477876+3.536116i | 9.477976+2.528777i | [12 empty] | 27.4 | 9.8489
[57 empty] | 27 | 0.0001-0.999877i | 0.000000001 | 0.010799+29.156419i | 10.798674+0.0001i |  | 0.010799+29.156419i | 0.113699+314.850665i | 10.809473+29.156519i | 9.495014+3.516277i | 9.495114+2.5164i | [12 empty] | 27.6 | 9.8615
[57 empty] | 27.2 | 0.0001-0.992525i | 0.000000001 | 0.010799+29.372392i | 10.798674+0.0001i |  | 0.010799+29.372392i | 0.113678+317.182887i | 10.809473+29.372492i | 9.511836+3.496614i | 9.511936+2.504089i | [12 empty] | 27.8 | 9.8739
[57 empty] | 27.4 | 0.0001-0.98528i | 0.000000001 | 0.010799+29.588366i | 10.798674+0.0001i |  | 0.010799+29.588366i | 0.113656+319.51512i | 10.809473+29.588466i | 9.528349+3.477124i | 9.528449+2.491844i | [12 empty] | 28 | 9.886
| If the watt losses in an HP filter resistor become excessive due to a low damping factor, VarStec recommends switching to a C-HP filter design, especially for tuning at or below the 5th harmonic. As a guideline, when resistor losses exceed roughly 100 kW per phase, a C-HP design should be strongly considered. C-HP filters exhibit near-zero losses at 60 Hz and permit very low damping factors, providing significantly improved resonance damping. | [55 empty] | 27.6 | 0.0001-0.978141i | 0.000000001 | 0.010799+29.804339i | 10.798674+0.0001i |  | 0.010799+29.804339i | 0.113634+321.847342i | 10.809473+29.804439i | 9.54456+3.457808i | 9.54466+2.479667i | [12 empty] | 28.2 | 9.8979
[57 empty] | 27.8 | 0.0001-0.971104i | 0.000000001 | 0.010799+30.020313i | 10.798674+0.0001i |  | 0.010799+30.020313i | 0.113613+324.179575i | 10.809473+30.020413i | 9.560476+3.438663i | 9.560576+2.467559i | [12 empty] | 28.4 | 9.9096
[57 empty] | 28 | 0.0001-0.964167i | 0.000000001 | 0.010799+30.236286i | 10.798674+0.0001i |  | 0.010799+30.236286i | 0.113591+326.511797i | 10.809473+30.236386i | 9.576103+3.419689i | 9.576203+2.455522i | [12 empty] | 28.6 | 9.9211
[57 empty] | 28.2 | 0.0001-0.957329i | 0.000000001 | 0.010799+30.45226i | 10.798674+0.0001i |  | 0.010799+30.45226i | 0.11357+328.844029i | 10.809473+30.45236i | 9.591449+3.400884i | 9.591549+2.443555i | [12 empty] | 28.8 | 9.9323
[57 empty] | 28.4 | 0.0001-0.950587i | 0.000000001 | 0.010799+30.668233i | 10.798674+0.0001i |  | 0.010799+30.668233i | 0.113548+331.176251i | 10.809473+30.668333i | 9.60652+3.382247i | 9.60662+2.43166i | [12 empty] | 29 | 9.9433
|  | Info@VarStec.com | [30 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 6 ¦ P a g e |  |  |  |  | 28.6 | 0.0001-0.94394i | 0.000000001 | 0.010799+30.884207i | 10.798674+0.0001i |  | 0.010799+30.884207i | 0.113526+333.508484i | 10.809473+30.884307i | 9.621321+3.363776i | 9.621421+2.419836i | [12 empty] | 29.2 | 9.9542
[57 empty] | 28.8 | 0.0001-0.937385i | 0.000000001 | 0.010799+31.10018i | 10.798674+0.0001i |  | 0.010799+31.10018i | 0.113505+335.840706i | 10.809473+31.10028i | 9.63586+3.34547i | 9.63596+2.408085i | [12 empty] | 29.4 | 9.9648
[57 empty] | 29 | 0.0001-0.93092i | 0.000000001 | 0.010799+31.316153i | 10.798674+0.0001i |  | 0.010799+31.316153i | 0.113483+338.172928i | 10.809473+31.316253i | 9.650141+3.327328i | 9.650241+2.396408i | [12 empty] | 29.6 | 9.9752
[57 empty] | 29.2 | 0.0001-0.924544i | 0.000000001 | 0.010799+31.532127i | 10.798674+0.0001i |  | 0.010799+31.532127i | 0.113462+340.505161i | 10.809473+31.532227i | 9.664171+3.309349i | 9.664271+2.384805i | [12 empty] | 29.8 | 9.9855
[57 empty] | 29.4 | 0.0001-0.918255i | 0.000000001 | 0.010799+31.7481i | 10.798674+0.0001i |  | 0.010799+31.7481i | 0.11344+342.837383i | 10.809473+31.7482i | 9.677956+3.29153i | 9.678056+2.373275i | [12 empty] | 30 | 9.9955
[57 empty] | 29.6 | 0.0001-0.91205i | 0.000000001 | 0.010799+31.964074i | 10.798674+0.0001i |  | 0.010799+31.964074i | 0.113418+345.169616i | 10.809473+31.964174i | 9.6915+3.273871i | 9.6916+2.361821i | [12 empty] | 30.2 | 10.0054
| Enter Customer PO # ¦ Stage 1 | [32 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 29.8 | 0.0001-0.905929i | 0.000000001 | 0.010799+32.180047i | 10.798674+0.0001i |  | 0.010799+32.180047i | 0.113397+347.501838i | 10.809473+32.180147i | 9.704809+3.25637i | 9.704909+2.350441i | [12 empty] | 30.4 | 10.0151
[57 empty] | 30 | 0.0001-0.899889i | 0.000000001 | 0.010799+32.396021i | 10.798674+0.0001i |  | 0.010799+32.396021i | 0.113375+349.834071i | 10.809473+32.396121i | 9.717889+3.239026i | 9.717989+2.339137i | [12 empty] | 30.6 | 10.0247
[34 empty] | Nomenclature and Parameter Definitions for Harmonic Filter Design | [22 empty] | 30.2 | 0.0001-0.89393i | 0.000000001 | 0.010799+32.611994i | 10.798674+0.0001i |  | 0.010799+32.611994i | 0.113354+352.166293i | 10.809473+32.612094i | 9.730744+3.221837i | 9.730844+2.327907i | [12 empty] | 30.8 | 10.034
[36 empty] | Xeff: |  | Effective reactance of the harmonic filter | [18 empty] | 30.4 | 0.0001-0.888049i | 0.000000001 | 0.010799+32.827968i | 10.798674+0.0001i |  | 0.010799+32.827968i | 0.113332+354.498526i | 10.809473+32.828068i | 9.743379+3.204802i | 9.743479+2.316753i | [12 empty] | 31 | 10.0432
[36 empty] | Qeff: |  | Effective reactive power output of the harmonic filter (considering fundamental current only) | [18 empty] | 30.6 | 0.0001-0.882245i | 0.000000001 | 0.010799+33.043941i | 10.798674+0.0001i |  | 0.010799+33.043941i | 0.11331+356.830748i | 10.809473+33.044041i | 9.755799+3.187919i | 9.755899+2.305674i | [12 empty] | 31.2 | 10.0522
[36 empty] | QRATED PER PHASE: |  | kvar rating of main capacitor group at their rated voltage (not the application voltage) | [18 empty] | 30.8 | 0.0001-0.876516i | 0.000000001 | 0.010799+33.259915i | 10.798674+0.0001i |  | 0.010799+33.259915i | 0.113289+359.16298i | 10.809473+33.260015i | 9.768009+3.171187i | 9.768109+2.294671i | [12 empty] | 31.4 | 10.0611
[36 empty] | VLLSYS: |  | Nominal system line-to-line voltage | [18 empty] | 31 | 0.0001-0.870861i | 0.000000001 | 0.010799+33.475888i | 10.798674+0.0001i |  | 0.010799+33.475888i | 0.113267+361.495202i | 10.809473+33.475988i | 9.780013+3.154605i | 9.780113+2.283744i | [12 empty] | 31.6 | 10.0698
[36 empty] | XC: |  | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [18 empty] | 31.2 | 0.0001-0.865278i | 0.000000001 | 0.010799+33.691862i | 10.798674+0.0001i |  | 0.010799+33.691862i | 0.113246+363.827435i | 10.809473+33.691962i | 9.791815+3.13817i | 9.791915+2.272892i | [12 empty] | 31.8 | 10.0784
[36 empty] | XL: |  | Inductive reactance of the harmonic filter reactor at fundamental frequency | [18 empty] | 31.4 | 0.0001-0.859767i | 0.000000001 | 0.010799+33.907835i | 10.798674+0.0001i |  | 0.010799+33.907835i | 0.113224+366.159657i | 10.809473+33.907935i | 9.803421+3.121882i | 9.803521+2.262115i | [12 empty] | 32 | 10.0868
[36 empty] | hn: |  | harmonic number of filter tuning point | [18 empty] | 31.6 | 0.0001-0.854325i | 0.000000001 | 0.010799+34.123809i | 10.798674+0.0001i |  | 0.010799+34.123809i | 0.113202+368.49189i | 10.809473+34.123909i | 9.814833+3.10574i | 9.814933+2.251415i | [12 empty] | 32.2 | 10.0951
[36 empty] | hf: |  | harmonic frequency of filter tuning point in Hertz | [18 empty] | 31.8 | 0.0001-0.848952i | 0.000000001 | 0.010799+34.339782i | 10.798674+0.0001i |  | 0.010799+34.339782i | 0.113181+370.824112i | 10.809473+34.339882i | 9.826057+3.08974i | 9.826157+2.240788i | [12 empty] | 32.4 | 10.1033
[36 empty] | f: |  | frequency | [18 empty] | 32 | 0.0001-0.843646i | 0.000000001 | 0.010799+34.555756i | 10.798674+0.0001i |  | 0.010799+34.555756i | 0.113159+373.156345i | 10.809473+34.555856i | 9.837096+3.073883i | 9.837196+2.230237i | [12 empty] | 32.6 | 10.1113
[36 empty] | HL: |  | Tuning Reactor Henry rating (millihenries) | [18 empty] | 32.2 | 0.0001-0.838406i | 0.000000001 | 0.010799+34.771729i | 10.798674+0.0001i |  | 0.010799+34.771729i | 0.113138+375.488567i | 10.809473+34.771829i | 9.847955+3.058167i | 9.848055+2.219761i | [12 empty] | 32.8 | 10.1191
[36 empty] | IRATED FUNDAMENTAL : |  | Fundamental current rating of filter bank | [18 empty] | 32.4 | 0.0001-0.833231i | 0.000000001 | 0.010799+34.987703i | 10.798674+0.0001i |  | 0.010799+34.987703i | 0.113116+377.8208i | 10.809473+34.987803i | 9.858636+3.04259i | 9.858736+2.209359i | [12 empty] | 33 | 10.1269
[35 empty] | VCAP FUNDAMENTAL VOLTAGE: |  |  | Fundamental voltage drop across capacitor | [18 empty] | 32.6 | 0.0001-0.828119i | 0.000000001 | 0.010799+35.203676i | 10.798674+0.0001i |  | 0.010799+35.203676i | 0.113095+380.153022i | 10.809473+35.203776i | 9.869143+3.027151i | 9.869243+2.199032i | [12 empty] | 33.2 | 10.1345
[36 empty] | VCAP HARMONIC VOLTAGE: |  | Harmonic voltage drop across capacitor | [18 empty] | 32.8 | 0.0001-0.82307i | 0.000000001 | 0.010799+35.419649i | 10.798674+0.0001i |  | 0.010799+35.419649i | 0.113073+382.485244i | 10.809473+35.419749i | 9.879481+3.011848i | 9.879581+2.188778i | [12 empty] | 33.4 | 10.142
| 🧮 FORMULAS | [34 empty] | VCAP RMS VOLTAGE: |  | Capacitor RMS voltage (fundamental voltage + harmonic voltages) | [18 empty] | 33 | 0.0001-0.818081i | 0.000000001 | 0.010799+35.635623i | 10.798674+0.0001i |  | 0.010799+35.635623i | 0.113051+384.817477i | 10.809473+35.635723i | 9.889653+2.996681i | 9.889753+2.1786i | [12 empty] | 33.6 | 10.1493
[36 empty] | VPEAK CAP VOLTAGE: |  | Capacitor voltage assuming or harmonics are coincident | [18 empty] | 33.2 | 0.0001-0.813153i | 0.000000001 | 0.010799+35.851596i | 10.798674+0.0001i |  | 0.010799+35.851596i | 0.11303+387.149699i | 10.809473+35.851696i | 9.899662+2.981647i | 9.899762+2.168494i | [12 empty] | 33.8 | 10.1566
| The below shows how a 1000 kvar 13.8kV 4.7th tuned HP Filter Design is computed manually and is the basis this spreadsheet. | [35 empty] | VCAP MAIN RMS VOLTAGE: | Capacitor RMS voltage including harmonics | [18 empty] | 33.4 | 0.0001-0.808284i | 0.000000001 | 0.010799+36.06757i | 10.798674+0.0001i |  | 0.010799+36.06757i | 0.113008+389.481931i | 10.809473+36.06767i | 9.909511+2.966745i | 9.909611+2.158461i | [12 empty] | 34 | 10.1637
[37 empty] | VCAP MAIN, PEAK CAP VOLTAGE: | Capacitor peak voltage, including harmonics, and assuming peaks are in phase. | [18 empty] | 33.6 | 0.0001-0.803473i | 0.000000001 | 0.010799+36.283543i | 10.798674+0.0001i |  | 0.010799+36.283543i | 0.112987+391.814154i | 10.809473+36.283643i | 9.919204+2.951974i | 9.919304+2.148501i | [12 empty] | 34.2 | 10.1707
[36 empty] | N: |  | Number of capacitors per phase | [18 empty] | 33.8 | 0.0001-0.798718i | 0.000000001 | 0.010799+36.499517i | 10.798674+0.0001i |  | 0.010799+36.499517i | 0.112965+394.146386i | 10.809473+36.499617i | 9.928744+2.937333i | 9.928844+2.138615i | [12 empty] | 34.4 | 10.1776
[36 empty] | VCAP VAR RATING: |  | Capacitor can var rating (in Kvar) | [18 empty] | 34 | 0.0001-0.79402i | 0.000000001 | 0.010799+36.71549i | 10.798674+0.0001i |  | 0.010799+36.71549i | 0.112943+396.478608i | 10.809473+36.71559i | 9.938134+2.92282i | 9.938234+2.1288i | [12 empty] | 34.6 | 10.1843
[36 empty] | ICAP RMS CURRENT: |  | RMS current seen by capacitor (amps rms) | [18 empty] | 34.2 | 0.0001-0.789377i | 0.000000001 | 0.010799+36.931464i | 10.798674+0.0001i |  | 0.010799+36.931464i | 0.112922+398.810841i | 10.809473+36.931564i | 9.947378+2.908433i | 9.947478+2.119056i | [12 empty] | 34.8 | 10.191
[36 empty] | IFILTER RMS CURRENT: |  | RMS current into filter branch (amps rms) | [18 empty] | 34.4 | 0.0001-0.784787i | 0.000000001 | 0.010799+37.147437i | 10.798674+0.0001i |  | 0.010799+37.147437i | 0.1129+401.143063i | 10.809473+37.147537i | 9.956477+2.894172i | 9.956577+2.109385i | [12 empty] | 35 | 10.1976
[36 empty] | DF: |  | Damping Factor is R/XLn at the tuning harmonic number (hn), where XLn=XL x hn | [18 empty] | 34.6 | 0.0001-0.780251i | 0.000000001 | 0.010799+37.363411i | 10.798674+0.0001i |  | 0.010799+37.363411i | 0.112879+403.475296i | 10.809473+37.363511i | 9.965435+2.880035i | 9.965535+2.099784i | [12 empty] | 35.2 | 10.204
[37 empty] | R | Resistance of high-pass damping resistor | [18 empty] | 34.8 | 0.0001-0.775767i | 0.000000001 | 0.010799+37.579384i | 10.798674+0.0001i |  | 0.010799+37.579384i | 0.112857+405.807518i | 10.809473+37.579484i | 9.974255+2.866021i | 9.974355+2.090254i | [12 empty] | 35.4 | 10.2104
[37 empty] | In | Current in amps at each harmonic | [18 empty] | 35 | 0.0001-0.771334i | 0.000000001 | 0.010799+37.795358i | 10.798674+0.0001i |  | 0.010799+37.795358i | 0.112835+408.139751i | 10.809473+37.795458i | 9.982939+2.852128i | 9.983039+2.080794i | [12 empty] | 35.6 | 10.2167
[57 empty] | 35.2 | 0.0001-0.766951i | 0.000000001 | 0.010799+38.011331i | 10.798674+0.0001i |  | 0.010799+38.011331i | 0.112814+410.471973i | 10.809473+38.011431i | 9.991491+2.838355i | 9.991591+2.071404i | [12 empty] | 35.8 | 10.2228
[34 empty] | Disclaimer and Use Limitation | [22 empty] | 35.4 | 0.0001-0.762618i | 0.000000001 | 0.010799+38.227305i | 10.798674+0.0001i |  | 0.010799+38.227305i | 0.112792+412.804206i | 10.809473+38.227405i | 9.999912+2.824701i | 10.000012+2.062083i | [12 empty] | 36 | 10.2289
[34 empty] | This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool. | [22 empty] | 35.6 | 0.0001-0.758334i | 0.000000001 | 0.010799+38.443278i | 10.798674+0.0001i |  | 0.010799+38.443278i | 0.112771+415.136428i | 10.809473+38.443378i | 10.008205+2.811164i | 10.008305+2.05283i | [12 empty] | 36.2 | 10.2349
[57 empty] | 35.8 | 0.0001-0.754097i | 0.000000001 | 0.010799+38.659252i | 10.798674+0.0001i |  | 0.010799+38.659252i | 0.112749+417.468661i | 10.809473+38.659352i | 10.016374+2.797744i | 10.016474+2.043647i | [12 empty] | 36.4 | 10.2407
[57 empty] | 36 | 0.0001-0.749908i | 0.000000001 | 0.010799+38.875225i | 10.798674+0.0001i |  | 0.010799+38.875225i | 0.112727+419.800883i | 10.809473+38.875325i | 10.02442+2.784439i | 10.02452+2.034531i | [12 empty] | 36.6 | 10.2465
[57 empty] | 36.2 | 0.0001-0.745765i | 0.000000001 | 0.010799+39.091198i | 10.798674+0.0001i |  | 0.010799+39.091198i | 0.112706+422.133105i | 10.809473+39.091298i | 10.032345+2.771247i | 10.032445+2.025482i | [12 empty] | 36.8 | 10.2522
[57 empty] | 36.4 | 0.0001-0.741667i | 0.000000001 | 0.010799+39.307172i | 10.798674+0.0001i |  | 0.010799+39.307172i | 0.112684+424.465337i | 10.809473+39.307272i | 10.040152+2.758168i | 10.040252+2.016501i | [12 empty] | 37 | 10.2579
| One-Line Diagram High-Pass Filter Design Parameters | [55 empty] | 36.6 | 0.0001-0.737614i | 0.000000001 | 0.010799+39.523145i | 10.798674+0.0001i |  | 0.010799+39.523145i | 0.112663+426.797559i | 10.809473+39.523245i | 10.047844+2.745201i | 10.047944+2.007587i | [12 empty] | 37.2 | 10.2634
[57 empty] | 36.8 | 0.0001-0.733606i | 0.000000001 | 0.010799+39.739119i | 10.798674+0.0001i |  | 0.010799+39.739119i | 0.112641+429.129792i | 10.809473+39.739219i | 10.055422+2.732343i | 10.055522+1.998737i | [12 empty] | 37.4 | 10.2688
[57 empty] | 37 | 0.0001-0.72964i | 0.000000001 | 0.010799+39.955092i | 10.798674+0.0001i |  | 0.010799+39.955092i | 0.112619+431.462014i | 10.809473+39.955192i | 10.062888+2.719594i | 10.062988+1.989954i | [12 empty] | 37.6 | 10.2742
[57 empty] | 37.2 | 0.0001-0.725717i | 0.000000001 | 0.010799+40.171066i | 10.798674+0.0001i |  | 0.010799+40.171066i | 0.112598+433.794247i | 10.809473+40.171166i | 10.070246+2.706953i | 10.070346+1.981236i | [12 empty] | 37.8 | 10.2795
[57 empty] | 37.4 | 0.0001-0.721836i | 0.000000001 | 0.010799+40.387039i | 10.798674+0.0001i |  | 0.010799+40.387039i | 0.112576+436.126469i | 10.809473+40.387139i | 10.077496+2.694418i | 10.077596+1.972582i | [12 empty] | 38 | 10.2847
[57 empty] | 37.6 | 0.0001-0.717997i | 0.000000001 | 0.010799+40.603013i | 10.798674+0.0001i |  | 0.010799+40.603013i | 0.112555+438.458702i | 10.809473+40.603113i | 10.084641+2.681989i | 10.084741+1.963992i | [12 empty] | 38.2 | 10.2898
[57 empty] | 37.8 | 0.0001-0.714198i | 0.000000001 | 0.010799+40.818986i | 10.798674+0.0001i |  | 0.010799+40.818986i | 0.112533+440.790924i | 10.809473+40.819086i | 10.091683+2.669664i | 10.091783+1.955466i | [12 empty] | 38.4 | 10.2949
[57 empty] | 38 | 0.0001-0.710439i | 0.000000001 | 0.010799+41.03496i | 10.798674+0.0001i |  | 0.010799+41.03496i | 0.112511+443.123157i | 10.809473+41.03506i | 10.098623+2.657442i | 10.098723+1.947003i | [12 empty] | 38.6 | 10.2999
[57 empty] | 38.2 | 0.0001-0.706719i | 0.000000001 | 0.010799+41.250933i | 10.798674+0.0001i |  | 0.010799+41.250933i | 0.11249+445.455379i | 10.809473+41.251033i | 10.105464+2.645322i | 10.105564+1.938603i | [12 empty] | 38.8 | 10.3048
|  | Info@VarStec.com | [30 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 8 ¦ P a g e |  |  |  |  | 38.4 | 0.0001-0.703039i | 0.000000001 | 0.010799+41.466907i | 10.798674+0.0001i |  | 0.010799+41.466907i | 0.112468+447.787612i | 10.809473+41.467007i | 10.112208+2.633302i | 10.112308+1.930263i | [12 empty] | 39 | 10.3096
[57 empty] | 38.6 | 0.0001-0.699396i | 0.000000001 | 0.010799+41.68288i | 10.798674+0.0001i |  | 0.010799+41.68288i | 0.112447+450.119834i | 10.809473+41.68298i | 10.118856+2.621383i | 10.118956+1.921987i | [12 empty] | 39.2 | 10.3144
[57 empty] | 38.8 | 0.0001-0.695791i | 0.000000001 | 0.010799+41.898854i | 10.798674+0.0001i |  | 0.010799+41.898854i | 0.112425+452.452066i | 10.809473+41.898954i | 10.12541+2.609562i | 10.12551+1.913771i | [12 empty] | 39.4 | 10.3191
[57 empty] | 39 | 0.0001-0.692223i | 0.000000001 | 0.010799+42.114827i | 10.798674+0.0001i |  | 0.010799+42.114827i | 0.112403+454.784288i | 10.809473+42.114927i | 10.131871+2.597839i | 10.131971+1.905616i | [12 empty] | 39.6 | 10.3237
[57 empty] | 39.2 | 0.0001-0.688691i | 0.000000001 | 0.010799+42.330801i | 10.798674+0.0001i |  | 0.010799+42.330801i | 0.112382+457.116521i | 10.809473+42.330901i | 10.138242+2.586212i | 10.138342+1.897521i | [12 empty] | 39.8 | 10.3283
[57 empty] | 39.4 | 0.0001-0.685195i | 0.000000001 | 0.010799+42.546774i | 10.798674+0.0001i |  | 0.010799+42.546774i | 0.11236+459.448743i | 10.809473+42.546874i | 10.144524+2.57468i | 10.144624+1.889485i | [12 empty] | 40 | 10.3328
[57 empty] | 39.6 | 0.0001-0.681734i | 0.000000001 | 0.010799+42.762748i | 10.798674+0.0001i |  | 0.010799+42.762748i | 0.112339+461.780976i | 10.809473+42.762848i | 10.150719+2.563243i | 10.150819+1.881509i | [12 empty] | 40.2 | 10.3372
[57 empty] | 39.8 | 0.0001-0.678309i | 0.000000001 | 0.010799+42.978721i | 10.798674+0.0001i |  | 0.010799+42.978721i | 0.112317+464.113198i | 10.809473+42.978821i | 10.156828+2.5519i | 10.156928+1.873591i | [12 empty] | 40.4 | 10.3416
[57 empty] | 40 | 0.0001-0.674917i | 0.000000001 | 0.010799+43.194694i | 10.798674+0.0001i |  | 0.010799+43.194694i | 0.112295+466.44542i | 10.809473+43.194794i | 10.162853+2.540649i | 10.162953+1.865732i | [12 empty] | 40.6 | 10.3459
[57 empty] | 40.2 | 0.0001-0.671559i | 0.000000001 | 0.010799+43.410668i | 10.798674+0.0001i |  | 0.010799+43.410668i | 0.112274+468.777653i | 10.809473+43.410768i | 10.168795+2.529489i | 10.168895+1.85793i | [12 empty] | 40.8 | 10.3502
[57 empty] | 40.4 | 0.0001-0.668235i | 0.000000001 | 0.010799+43.626641i | 10.798674+0.0001i |  | 0.010799+43.626641i | 0.112252+471.109875i | 10.809473+43.626741i | 10.174656+2.518419i | 10.174756+1.850184i | [12 empty] | 41 | 10.3544
[57 empty] | 40.6 | 0.0001-0.664943i | 0.000000001 | 0.010799+43.842615i | 10.798674+0.0001i |  | 0.010799+43.842615i | 0.112231+473.442108i | 10.809473+43.842715i | 10.180437+2.507439i | 10.180537+1.842496i | [12 empty] | 41.2 | 10.3585
[57 empty] | 40.8 | 0.0001-0.661683i | 0.000000001 | 0.010799+44.058588i | 10.798674+0.0001i |  | 0.010799+44.058588i | 0.112209+475.77433i | 10.809473+44.058688i | 10.18614+2.496547i | 10.18624+1.834864i | [12 empty] | 41.4 | 10.3626
[57 empty] | 41 | 0.0001-0.658456i | 0.000000001 | 0.010799+44.274562i | 10.798674+0.0001i |  | 0.010799+44.274562i | 0.112187+478.106563i | 10.809473+44.274662i | 10.191766+2.485743i | 10.191866+1.827287i | [12 empty] | 41.6 | 10.3666
[57 empty] | 41.2 | 0.0001-0.655259i | 0.000000001 | 0.010799+44.490535i | 10.798674+0.0001i |  | 0.010799+44.490535i | 0.112166+480.438785i | 10.809473+44.490635i | 10.197316+2.475025i | 10.197416+1.819766i | [12 empty] | 41.8 | 10.3706
[57 empty] | 41.4 | 0.0001-0.652094i | 0.000000001 | 0.010799+44.706509i | 10.798674+0.0001i |  | 0.010799+44.706509i | 0.112144+482.771017i | 10.809473+44.706609i | 10.202792+2.464393i | 10.202892+1.812299i | [12 empty] | 42 | 10.3745
[57 empty] | 41.6 | 0.0001-0.648959i | 0.000000001 | 0.010799+44.922482i | 10.798674+0.0001i |  | 0.010799+44.922482i | 0.112123+485.103239i | 10.809473+44.922582i | 10.208195+2.453846i | 10.208295+1.804887i | [12 empty] | 42.2 | 10.3784
[57 empty] | 41.8 | 0.0001-0.645854i | 0.000000001 | 0.010799+45.138456i | 10.798674+0.0001i |  | 0.010799+45.138456i | 0.112101+487.435472i | 10.809473+45.138556i | 10.213526+2.443382i | 10.213626+1.797528i | [12 empty] | 42.4 | 10.3822
[57 empty] | 42 | 0.0001-0.642778i | 0.000000001 | 0.010799+45.354429i | 10.798674+0.0001i |  | 0.010799+45.354429i | 0.112079+489.767694i | 10.809473+45.354529i | 10.218786+2.433001i | 10.218886+1.790223i | [12 empty] | 42.6 | 10.386
[57 empty] | 42.2 | 0.0001-0.639732i | 0.000000001 | 0.010799+45.570403i | 10.798674+0.0001i |  | 0.010799+45.570403i | 0.112058+492.099927i | 10.809473+45.570503i | 10.223977+2.422702i | 10.224077+1.78297i | [12 empty] | 42.8 | 10.3897
[57 empty] | 42.4 | 0.0001-0.636714i | 0.000000001 | 0.010799+45.786376i | 10.798674+0.0001i |  | 0.010799+45.786376i | 0.112036+494.432149i | 10.809473+45.786476i | 10.229101+2.412484i | 10.229201+1.77577i | [12 empty] | 43 | 10.3933
[57 empty] | 42.6 | 0.0001-0.633725i | 0.000000001 | 0.010799+46.00235i | 10.798674+0.0001i |  | 0.010799+46.00235i | 0.112015+496.764382i | 10.809473+46.00245i | 10.234157+2.402347i | 10.234257+1.768622i | [12 empty] | 43.2 | 10.3969
[57 empty] | 42.8 | 0.0001-0.630764i | 0.000000001 | 0.010799+46.218323i | 10.798674+0.0001i |  | 0.010799+46.218323i | 0.111993+499.096604i | 10.809473+46.218423i | 10.239147+2.392288i | 10.239247+1.761524i | [12 empty] | 43.4 | 10.4005
[57 empty] | 43 | 0.0001-0.62783i | 0.000000001 | 0.010799+46.434297i | 10.798674+0.0001i |  | 0.010799+46.434297i | 0.111971+501.428837i | 10.809473+46.434397i | 10.244073+2.382308i | 10.244173+1.754478i | [12 empty] | 43.6 | 10.404
[57 empty] | 43.2 | 0.0001-0.624923i | 0.000000001 | 0.010799+46.65027i | 10.798674+0.0001i |  | 0.010799+46.65027i | 0.11195+503.761059i | 10.809473+46.65037i | 10.248935+2.372406i | 10.249035+1.747483i | [12 empty] | 43.8 | 10.4075
[57 empty] | 43.4 | 0.0001-0.622043i | 0.000000001 | 0.010799+46.866243i | 10.798674+0.0001i |  | 0.010799+46.866243i | 0.111928+506.093281i | 10.809473+46.866343i | 10.253734+2.362581i | 10.253834+1.740538i | [12 empty] | 44 | 10.4109
[57 empty] | 43.6 | 0.0001-0.61919i | 0.000000001 | 0.010799+47.082217i | 10.798674+0.0001i |  | 0.010799+47.082217i | 0.111907+508.425514i | 10.809473+47.082317i | 10.258472+2.352832i | 10.258572+1.733642i | [12 empty] | 44.2 | 10.4143
[57 empty] | 43.8 | 0.0001-0.616363i | 0.000000001 | 0.010799+47.29819i | 10.798674+0.0001i |  | 0.010799+47.29819i | 0.111885+510.757736i | 10.809473+47.29829i | 10.26315+2.343158i | 10.26325+1.726795i | [12 empty] | 44.4 | 10.4177
[57 empty] | 44 | 0.0001-0.613561i | 0.000000001 | 0.010799+47.514164i | 10.798674+0.0001i |  | 0.010799+47.514164i | 0.111863+513.089968i | 10.809473+47.514264i | 10.267768+2.333558i | 10.267868+1.719997i | [12 empty] | 44.6 | 10.421
[57 empty] | 44.2 | 0.0001-0.610785i | 0.000000001 | 0.010799+47.730137i | 10.798674+0.0001i |  | 0.010799+47.730137i | 0.111842+515.422191i | 10.809473+47.730237i | 10.272328+2.324032i | 10.272428+1.713247i | [12 empty] | 44.8 | 10.4242
[57 empty] | 44.4 | 0.0001-0.608033i | 0.000000001 | 0.010799+47.946111i | 10.798674+0.0001i |  | 0.010799+47.946111i | 0.11182+517.754423i | 10.809473+47.946211i | 10.27683+2.314579i | 10.27693+1.706546i | [12 empty] | 45 | 10.4274
[57 empty] | 44.6 | 0.0001-0.605307i | 0.000000001 | 0.010799+48.162084i | 10.798674+0.0001i |  | 0.010799+48.162084i | 0.111799+520.086645i | 10.809473+48.162184i | 10.281275+2.305198i | 10.281375+1.699891i | [12 empty] | 45.2 | 10.4306
[57 empty] | 44.8 | 0.0001-0.602605i | 0.000000001 | 0.010799+48.378058i | 10.798674+0.0001i |  | 0.010799+48.378058i | 0.111777+522.418878i | 10.809473+48.378158i | 10.285665+2.295888i | 10.285765+1.693283i | [12 empty] | 45.4 | 10.4337
[57 empty] | 45 | 0.0001-0.599926i | 0.000000001 | 0.010799+48.594031i | 10.798674+0.0001i |  | 0.010799+48.594031i | 0.111755+524.7511i | 10.809473+48.594131i | 10.29+2.286649i | 10.2901+1.686723i | [12 empty] | 45.6 | 10.4368
[57 empty] | 45.2 | 0.0001-0.597272i | 0.000000001 | 0.010799+48.810005i | 10.798674+0.0001i |  | 0.010799+48.810005i | 0.111734+527.083333i | 10.809473+48.810105i | 10.294282+2.27748i | 10.294382+1.680208i | [12 empty] | 45.8 | 10.4399
[57 empty] | 45.4 | 0.0001-0.594641i | 0.000000001 | 0.010799+49.025978i | 10.798674+0.0001i |  | 0.010799+49.025978i | 0.111712+529.415555i | 10.809473+49.026078i | 10.29851+2.26838i | 10.29861+1.673739i | [12 empty] | 46 | 10.4429
[57 empty] | 45.6 | 0.0001-0.592033i | 0.000000001 | 0.010799+49.241952i | 10.798674+0.0001i |  | 0.010799+49.241952i | 0.111691+531.747788i | 10.809473+49.242052i | 10.302687+2.259348i | 10.302787+1.667315i | [12 empty] | 46.2 | 10.4459
[57 empty] | 45.8 | 0.0001-0.589447i | 0.000000001 | 0.010799+49.457925i | 10.798674+0.0001i |  | 0.010799+49.457925i | 0.111669+534.08001i | 10.809473+49.458025i | 10.306812+2.250384i | 10.306912+1.660937i | [12 empty] | 46.4 | 10.4488
[57 empty] | 46 | 0.0001-0.586884i | 0.000000001 | 0.010799+49.673899i | 10.798674+0.0001i |  | 0.010799+49.673899i | 0.111647+536.412243i | 10.809473+49.673999i | 10.310886+2.241487i | 10.310986+1.654603i | [12 empty] | 46.6 | 10.4517
[57 empty] | 46.2 | 0.0001-0.584344i | 0.000000001 | 0.010799+49.889872i | 10.798674+0.0001i |  | 0.010799+49.889872i | 0.111626+538.744465i | 10.809473+49.889972i | 10.314911+2.232656i | 10.315011+1.648312i | [12 empty] | 46.8 | 10.4546
[57 empty] | 46.4 | 0.0001-0.581825i | 0.000000001 | 0.010799+50.105846i | 10.798674+0.0001i |  | 0.010799+50.105846i | 0.111604+541.076698i | 10.809473+50.105946i | 10.318887+2.22389i | 10.318987+1.642065i | [12 empty] | 47 | 10.4574
[57 empty] | 46.6 | 0.0001-0.579328i | 0.000000001 | 0.010799+50.321819i | 10.798674+0.0001i |  | 0.010799+50.321819i | 0.111583+543.40892i | 10.809473+50.321919i | 10.322815+2.21519i | 10.322915+1.635862i | [12 empty] | 47.2 | 10.4602
[57 empty] | 46.8 | 0.0001-0.576852i | 0.000000001 | 0.010799+50.537793i | 10.798674+0.0001i |  | 0.010799+50.537793i | 0.111561+545.741152i | 10.809473+50.537893i | 10.326696+2.206554i | 10.326796+1.629702i | [12 empty] | 47.4 | 10.463
[57 empty] | 47 | 0.0001-0.574398i | 0.000000001 | 0.010799+50.753766i | 10.798674+0.0001i |  | 0.010799+50.753766i | 0.11154+548.073374i | 10.809473+50.753866i | 10.33053+2.197981i | 10.33063+1.623583i | [12 empty] | 47.6 | 10.4657
[57 empty] | 47.2 | 0.0001-0.571964i | 0.000000001 | 0.010799+50.969739i | 10.798674+0.0001i |  | 0.010799+50.969739i | 0.111518+550.405596i | 10.809473+50.969839i | 10.334319+2.189472i | 10.334419+1.617508i | [12 empty] | 47.8 | 10.4684
[57 empty] | 47.4 | 0.0001-0.56955i | 0.000000001 | 0.010799+51.185713i | 10.798674+0.0001i |  | 0.010799+51.185713i | 0.111496+552.737829i | 10.809473+51.185813i | 10.338062+2.181024i | 10.338162+1.611474i | [12 empty] | 48 | 10.4711
[57 empty] | 47.6 | 0.0001-0.567157i | 0.000000001 | 0.010799+51.401686i | 10.798674+0.0001i |  | 0.010799+51.401686i | 0.111475+555.070051i | 10.809473+51.401786i | 10.341761+2.172639i | 10.341861+1.605482i | [12 empty] | 48.2 | 10.4737
[57 empty] | 47.8 | 0.0001-0.564784i | 0.000000001 | 0.010799+51.61766i | 10.798674+0.0001i |  | 0.010799+51.61766i | 0.111453+557.402284i | 10.809473+51.61776i | 10.345416+2.164314i | 10.345516+1.59953i | [12 empty] | 48.4 | 10.4763
[57 empty] | 48 | 0.0001-0.562431i | 0.000000001 | 0.010799+51.833633i | 10.798674+0.0001i |  | 0.010799+51.833633i | 0.111432+559.734506i | 10.809473+51.833733i | 10.349028+2.15605i | 10.349128+1.593619i | [12 empty] | 48.6 | 10.4789
[57 empty] | 48.2 | 0.0001-0.560097i | 0.000000001 | 0.010799+52.049607i | 10.798674+0.0001i |  | 0.010799+52.049607i | 0.11141+562.066739i | 10.809473+52.049707i | 10.352597+2.147845i | 10.352697+1.587748i | [12 empty] | 48.8 | 10.4815
[57 empty] | 48.4 | 0.0001-0.557783i | 0.000000001 | 0.010799+52.26558i | 10.798674+0.0001i |  | 0.010799+52.26558i | 0.111388+564.398961i | 10.809473+52.26568i | 10.356125+2.1397i | 10.356225+1.581917i | [12 empty] | 49 | 10.484
[57 empty] | 48.6 | 0.0001-0.555487i | 0.000000001 | 0.010799+52.481554i | 10.798674+0.0001i |  | 0.010799+52.481554i | 0.111367+566.731194i | 10.809473+52.481654i | 10.359612+2.131613i | 10.359712+1.576126i | [12 empty] | 49.2 | 10.4865
[57 empty] | 48.8 | 0.0001-0.553211i | 0.000000001 | 0.010799+52.697527i | 10.798674+0.0001i |  | 0.010799+52.697527i | 0.111345+569.063416i | 10.809473+52.697627i | 10.363058+2.123584i | 10.363158+1.570373i | [12 empty] | 49.4 | 10.4889
[57 empty] | 49 | 0.0001-0.550953i | 0.000000001 | 0.010799+52.913501i | 10.798674+0.0001i |  | 0.010799+52.913501i | 0.111324+571.395649i | 10.809473+52.913601i | 10.366465+2.115613i | 10.366565+1.56466i | [12 empty] | 49.6 | 10.4913
[57 empty] | 49.2 | 0.0001-0.548713i | 0.000000001 | 0.010799+53.129474i | 10.798674+0.0001i |  | 0.010799+53.129474i | 0.111302+573.727871i | 10.809473+53.129574i | 10.369832+2.107698i | 10.369932+1.558985i | [12 empty] | 49.8 | 10.4937
[57 empty] | 49.4 | 0.0001-0.546492i | 0.000000001 | 0.010799+53.345448i | 10.798674+0.0001i |  | 0.010799+53.345448i | 0.11128+576.060103i | 10.809473+53.345548i | 10.373161+2.09984i | 10.373261+1.553348i | [12 empty] | 50 | 10.4961
[57 empty] | 49.6 | 0.0001-0.544288i | 0.000000001 | 0.010799+53.561421i | 10.798674+0.0001i |  | 0.010799+53.561421i | 0.111259+578.392325i | 10.809473+53.561521i | 10.376451+2.092037i | 10.376551+1.547749i
[57 empty] | 49.8 | 0.0001-0.542102i | 0.000000001 | 0.010799+53.777395i | 10.798674+0.0001i |  | 0.010799+53.777395i | 0.111237+580.724558i | 10.809473+53.777495i | 10.379704+2.08429i | 10.379804+1.542188i
[57 empty] | 50 | 0.0001-0.539934i | 0.000000001 | 0.010799+53.993368i | 10.798674+0.0001i |  | 0.010799+53.993368i | 0.111216+583.05678i | 10.809473+53.993468i | 10.38292+2.076597i | 10.38302+1.536663i
[61 empty] | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | 9.96
[59 empty] | VCAP HARMONIC VOLTAGE (volts)^2 |  | 56376516.1461 | 0 | 0 | 0 | 291528.3794 | 95192.9402 | 21683.929 | 4624 | 1008.7487 | 201.8895 | 137.7733 | 116.6114 | 0 | 0 | 59.4956 | 53.2375
[59 empty] | Filter Current (amps) (In)^2 |  | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 14.0834
[59 empty] | kvar (single phase) |  | 2088.2756 | 0 | 0 | 0 | 53.9934 | 24.6827 | 8.8353 | 1.869 | 0.63522 | 0.14209 | 0.11738 | 0.10799 | 0 | 0 | 0.077133 | 0.072964 | 73.7868
3674.5846
[59 empty] | harmonic # |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37
[59 empty] | Total filter amps |  | 278.1241 | 0 | 0 | 0 | 100 | 80 | 60 | 30 | 20 | 10 | 10 | 10 | 0 | 0 | 10 | 10
[59 empty] | R & X EQUIVALENT IMPEDANCE (ohms) |  | 1.0745 | 2.1178 | 3.103 | 4.0105 | 4.8293 | 6.1926 | 7.9904 | 8.5593 | 9.3077 | 9.5559 | 9.9031 | 10.0263 | 10.2088 | 10.2772 | 10.3832 | 10.4246
[59 empty] | I REACTOR (Calculate voltage then divide by xLn) |  | 276.7439 | 0 | 0 | 0 | 89.4427 | 65.5386 | 40.3604 | 18.2913 | 10.1404 | 4.6575 | 3.9873 | 3.7139 | 0 | 0 | 2.7472 | 2.6091
[59 empty] | I RESISTOR (calculate voltage then divide by R) |  | 27.6744 | 0 | 0 | 0 | 44.7214 | 45.877 | 44.3964 | 23.7787 | 17.2387 | 8.8492 | 9.1707 | 9.2848 | 0 | 0 | 9.6152 | 9.6536
[59 empty] | Resistor losses (watts) |  | 8270.3984 | 0 | 0 | 0 | 21597.3472 | 22727.9466 | 21284.6255 | 6105.8671 | 3209.066 | 845.6228 | 908.1873 | 930.9201 | 0 | 0 | 998.3679 | 1006.357 | 79614.3076 | 238842.9228
[59 empty] | I Resistor ^2 (watts) |  | 765.8717 | 0 | 0 | 0 | 2000 | 2104.698 | 1971.0407 | 565.4275 | 297.1722 | 78.308 | 84.1017 | 86.2069 | 0 | 0 | 92.4528 | 93.1926 | Resistor RMS Amps |  | 90.2135
[59 empty] | Total filter amps^2 |  | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | Total Filter RMS Amps |  | 314.8858
[59 empty] | I2R REACTOR LOSSES (watts) |  | 827.0398 | 0 | 0 | 0 | 86.3894 | 46.3836 | 17.5906 | 3.6129 | 1.1104 | 0.23424 | 0.17168 | 0.14895 | 0 | 0 | 0.081499 | 0.07351
[60 empty] | Reactor Current Squared | 76587.1685 | 0 | 0 | 0 | 8000 | 4295.302 | 1628.9593 | 334.5725 | 102.8278 | 21.692 | 15.8983 | 13.7931 | 0 | 0 | 7.5472 | 6.8074 | 301.6862
This spreadsheet is used to support the design, tuning, and component selection associated with HP harmonic filters as engineered by VarStec Power Solutions. It provides a consistent methodology for determining all electrical parameters required for proper filter performance, including reactances, inductance, capacitor reactive power and voltage ratings, harmonic currents, voltage stresses, and damping resistance. The summary below describes the calculation process applied throughout the tool using a 13.8kV 1000 kvar filter branch as an example. The tool assumes that harmonic simulations have been conducted and that the current spectrum into the harmonic filter is known. These values are inserted in the blue highlighted fields of rows 24 and 25 on page 1. For additional information, engineering support, or custom filter designs, contact VarStec Power Solutions at info@varstec.com. The design process begins by establishing the fundamental kvar requirement of the harmonic filter, typically based on the kvar demand of the connected load or the kvar allocation assigned to each stage of a multi-stage harmonic filter. This requirement is defined as and forms the foundation of all subsequent calculations. Using the system’s nominal line-to-line voltage , the spreadsheet determines the fundamental capacitive reactance of the capacitor section, . For a HP filter, this value directly represents XC and XL must be summed together as one subtracts from the other. Xeff=XL-XC and individually are calculated using the relationship .
This spreadsheet is used to support the design, tuning, and component selection associated with HP harmonic filters as engineered by VarStec Power Solutions. It provides a consistent methodology for determining all electrical parameters required for proper filter performance, including reactances, inductance, capacitor reactive power and voltage ratings, harmonic currents, voltage stresses, and damping resistance. The summary below describes the calculation process applied throughout the tool using a 13.8kV 1000 kvar filter branch as an example. The tool assumes that harmonic simulations have been conducted and that the current spectrum into the harmonic filter is known. These values are inserted in the blue highlighted fields of rows 24 and 25 on page 1. For additional information, engineering support, or custom filter designs, contact VarStec Power Solutions at info@varstec.com. The design process begins by establishing the fundamental kvar requirement of the harmonic filter, typically based on the kvar demand of the connected load or the kvar allocation assigned to each stage of a multi-stage harmonic filter. This requirement is defined as 𝑄_𝑒𝑓𝑓and forms the foundation of all subsequent calculations. Using the system’s nominal line-to-line voltage 𝑘𝑉_𝐿𝐿𝑆𝑌𝑆, the spreadsheet determines the fundamental capacitive reactance of the capacitor section, 𝑋_𝑒𝑓𝑓. For a HP filter, this value directly represents XC and XL must be summed together as one subtracts from the other. Xeff=XL-XC and individually are calculated using the relationship 𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓 .
The harmonic filter design must ensure capacitor operating duties stay within IEEE/IEC-rated limits, including the allowable 10% continuous overvoltage. The spreadsheet checks four key parameters against their rated duty: % Rated Volts, % Crest Voltage, % Amps, % kVAR. If any value exceeds its limit, the cell turns red. In that case, increase the capacitor voltage rating. The objective is to meet the required duty without significantly exceeding the rating, which would increase cost.
With XC known, XL is computed using the relationship: Xeff=XL-XC. From there L and C are calculated.
The capacitor kvar ratings is then determined using the rated operating voltage. The spreadsheet next evaluates the high-pass damping resistor. Its ohmic value is derived from the specified damping factor (DF) of the HP filter (determined from harmonic simulations), linking the resistor to the tuning reactance at the harmonic frequency. With kvar and reactances established, the spreadsheet computes the fundamental filter current and applies injected harmonic current data to evaluate the resulting capacitor voltage stresses, current duty, and reactive power duty. These computed values are compared against industry-standard capacitor ratings to confirm suitability for the intended application.
The spreadsheet then resolves the fundamental and harmonic currents flowing in the reactor, capacitor and high-pass resistors. This is performed using complex current-divider calculations to ensure accurate representation of harmonic behavior. The watt loss in the damping resistor is subsequently computed and verified against its thermal rating.
Taken together, these calculations define a complete, consistent, and repeatable VarStec methodology for the engineering of HP harmonic filters. The spreadsheet determines all critical design parameters, including reactances, inductance, kvar ratings, current loading, voltage stress, and damping characteristics, using standardized electrical notation to provide traceability, transparency, and field-proven reliability.
(ohms) =
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/𝑄_𝑒𝑓𝑓 (ohms) = 〖13.8〗^2/(1.0 )=190.4 (𝑜ℎ𝑚𝑠)
(ohms) = 190.4 (ohms)=199.4 (ohms)
𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓 (ohms) = (〖4.7〗^2/(〖4.7〗^2−1)) 190.4 (ohms)=199.4 (ohms)
=
𝑋_𝐿=𝑋_𝐶/ℎ^2 = 199.4/〖4.7〗^2 =9.03 𝑜ℎ𝑚𝑠
= 23.95 mH
𝐻(𝑖𝑛𝑑𝑢𝑐𝑡𝑎𝑛𝑐𝑒)=𝑋_𝐿/2𝜋𝑓×1000(𝑚𝐻)=9.03/(2𝜋 60)×1000(𝑚𝐻)= 23.95 mH
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒𝐼_𝑛^2 )
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆 )×1000=1.0/(1.73×13.8)×1000=41.88 𝑎𝑚𝑝𝑠
〖𝑄_(𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸 (𝑀𝑉𝐴𝑅)) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶 =(9.54)^2/199.47=0.456 𝑀𝑉𝐴𝑅/𝑃ℎ𝑎𝑠𝑒〗_
𝑄_𝑒𝑓𝑓=𝑂𝑢𝑡𝑝𝑢𝑡 𝑀𝑉𝐴𝑅 𝑅𝑎𝑡𝑖𝑛𝑔 𝑜𝑓 𝐹𝑖𝑙𝑡𝑒𝑟=(𝐷𝑒𝑠𝑖𝑟𝑒𝑑 3 𝑃ℎ𝑎𝑠𝑒 𝑘𝑣𝑎𝑟)/1000 =1.0 𝑀𝑉𝐴𝑅
k
k𝑉_𝐿𝐿𝑆𝑌𝑆=𝐹𝑖𝑙𝑡𝑒𝑟 𝑁𝑜𝑚𝑖𝑛𝑎𝑙 𝐿𝑖𝑛𝑒−𝑡𝑜−𝐿𝑖𝑛𝑒 𝑉𝑜𝑙𝑡𝑎𝑔𝑒 𝑅𝑎𝑡𝑖𝑛𝑔 (𝐾𝑉)=13.8 𝑘𝑉
(f)
𝐶=1/(2𝜋𝑓𝑋_𝑐 ) (f)
𝐿=𝑋_𝐿/2𝜋𝑓 (𝐻)
R
R=𝐷𝐹×𝑥_𝐿×ℎ (𝑜ℎ𝑚𝑠)
VLN
JXL
-JXC
R

## C-HP Filter Design
Impedance Calculations
[32 empty] | VarStec Power Solutions, Inc. | [24 empty] | PLOT (ohms) |  |  | (res branch) |  | (aux branch) | Resistance branch x AUX Branch | Resistance Branch + Aux Branch | Parallel Sum of Resistance Branch and AUX Branch | + Main Capacitor Branch | [5 empty] | SD - Standard Duty Capacitors
[32 empty] | PO Box 942 | [23 empty] | HARM # | Xc main | Xc aux | XL (inductance) | Resistance |  | XCAUX + XL | [9 empty] | HD- Heavy Duty Capacitor
[32 empty] | Saratoga Springs, NY 12866 | Enter Customer PO # ¦ Stage 1 | [22 empty] | 1 | 0.0001-25.916817i | 0.000001-1.079867i | 0.010799+1.079867i | 10.798674+0.0001i |  | 0.0108 | 0.116626+0.000001i | 10.809474+0.0001i | 0.010789 | 0.010889-25.916817i | 1 | 25.9168 |  |  |  | EXD - Extreme Duty Capacitors
[32 empty] | 518.369.7589 | [23 empty] | 1.2 | 0.0001-21.597347i | 0.000001-0.899889i | 0.010799+1.295841i | 10.798674+0.0001i |  | 0.0108+0.395952i | 0.116586+4.275758i | 10.809474+0.396052i | 0.025245+0.394632i | 0.025345-21.202715i | 1.2 | 21.2027
| Harmonic Filter Design / C-High-Pass (C-HP) Type | [31 empty] | 📐 DESIGN VERIFICATION | [22 empty] | 1.4 | 0.0001-18.512012i | 0.000001-0.771334i | 0.010799+1.511814i | 10.798674+0.0001i |  | 0.0108+0.74048i | 0.116552+7.996203i | 10.809474+0.74058i | 0.061176+0.735549i | 0.061276-17.776463i | 1.4 | 17.7766 |  |  |  | (Rw) (Resistor KW/Phase) |  | 200
[56 empty] | 1.6 | 0.0001-16.19801i | 0.000001-0.674917i | 0.010799+1.727788i | 10.798674+0.0001i |  | 0.0108+1.052871i | 0.11652+11.369612i | 10.809474+1.052971i | 0.112175+1.040892i | 0.112275-15.157118i | 1.6 | 15.1575
| 📜 PROJECT DETAILS | [29 empty] | April 19, 2026 |  | Main Capacitor Group Design Ratings Versus Duty Rating | [22 empty] | 1.8 | 0.0001-14.398231i | 0.000001-0.599926i | 0.010799+1.943761i | 10.798674+0.0001i |  | 0.0108+1.343835i | 0.116491+14.511637i | 10.809474+1.343935i | 0.174983+1.320737i | 0.175083-13.077494i | 1.8 | 13.0787
[40 empty] | Design Values | [15 empty] | 2 | 0.0001-12.958408i | 0.000001-0.539934i | 0.010799+2.159735i | 10.798674+0.0001i |  | 0.0108+1.619801i | 0.116464+17.491704i | 10.809474+1.619901i | 0.247711+1.581061i | 0.247811-11.377347i | 2 | 11.38
|  |  |  | Project Name: | Enter Project Name | [15 empty] | VarStec SO #: |  | Enter SO Number | [16 empty] | At Nominal Voltage | [5 empty] | At Nominal 110% System Voltage | [9 empty] | 2.2 | 0.0001-11.780371i | 0.000001-0.490849i | 0.010799+2.375708i | 10.798674+0.0001i |  | 0.0108+1.884859i | 0.116437+20.353979i | 10.809474+1.884959i | 0.329118+1.825584i | 0.329218-9.954787i | 2.2 | 9.9602
|  |  |  | Customer PO #: | Enter Customer PO # | [15 empty] | Revision #: |  | Rev 1 | [10 empty] | Design Parameter | [12 empty] | Rated Duty | [8 empty] | 2.4 | 0.0001-10.798674i | 0.000001-0.449945i | 0.010799+2.591682i | 10.798674+0.0001i |  | 0.0108+2.141737i | 0.116412+23.127921i | 10.809474+2.141837i | 0.418296+2.056714i | 0.418396-8.74196i | 2.4 | 8.752
|  |  |  | Tag #: | Enter Tag Number | [15 empty] | Stage/Branch: |  | Stage 1 | [14 empty] | % RATED VOLTS: |  | 72.64% | [5 empty] | 79.85% | 125% | [8 empty] | 2.6 | 0.0001-9.968006i | 0.000001-0.415334i | 0.010799+2.807655i | 10.798674+0.0001i |  | 0.0108+2.392321i | 0.116386+25.833896i | 10.809474+2.392421i | 0.514518+2.276055i | 0.514618-7.691951i | 2.6 | 7.7091
[38 empty] | % CREST VOLTAGE: |  | 83.37% | [5 empty] | 93.37% | 135% | [8 empty] | 2.8 | 0.0001-9.256006i | 0.000001-0.385667i | 0.010799+3.023629i | 10.798674+0.0001i |  | 0.0108+2.637962i | 0.116362+28.486493i | 10.809474+2.638062i | 0.61716+2.484708i | 0.61726-6.771298i | 2.8 | 6.7994
| 🧮 SPECIFICATION DETAILS | [36 empty] | % 60HZ AMPS: |  | 81.94% | [5 empty] | 88.39% | 135% | [8 empty] | 3 | 0.0001-8.638939i | 0.000001-0.359956i | 0.010799+3.239602i | 10.798674+0.0001i |  | 0.0108+2.879646i | 0.116338+31.096359i | 10.809474+2.879746i | 0.725658+2.683447i | 0.725758-5.955492i | 3 | 5.9996
|  | Key Filter Ratings | [35 empty] | % 60HZ KVAR: |  | 54.65% | [5 empty] | 65.64% | 135% | [8 empty] | 3.2 | 0.0001-8.099005i | 0.000001-0.337459i | 0.010799+3.455576i | 10.798674+0.0001i |  | 0.0108+3.118117i | 0.116314+33.67153i | 10.809474+3.118217i | 0.839489+2.872834i | 0.839589-5.226171i | 3.2 | 5.2932
[13 empty] | kVLLsys (System Line-to-Line Voltage Rating): | 12.47 |  | kV | [10 empty] | Xeff Filter Effective Reactance): | 25.9168 |  |  | Ohms | [24 empty] | 3.4 | 0.0001-7.622593i | 0.000001-0.317608i | 0.010799+3.671549i | 10.798674+0.0001i |  | 0.0108+3.353941i | 0.11629+36.218117i | 10.809474+3.354041i | 0.958154+3.053287i | 0.958254-4.569306i | 3.4 | 4.6687
|  |  | Qeff (3-Phase Output Rating of Filter): | [10 empty] | 6000 |  | kvar | [16 empty] | ICAP MAIN (Fundamental Current per Capacitor): | [8 empty] | 55.6248 |  |  | amps |  |  | Capacitive Reactance (per can): | 129.5841 | Ohms | [5 empty] | 3.6 | 0.0001-7.199116i | 0.000001-0.299963i | 0.010799+3.887523i | 10.798674+0.0001i |  | 0.0108+3.58756i | 0.116267+38.740892i | 10.809474+3.58766i | 1.081177+3.225134i | 1.081277-3.973982i | 3.6 | 4.1185
|  |  | hn (Tuning Point of Filter): | [10 empty] | 5 |  | (harmonic number) | [10 empty] | hf : | 300 |  |  | Hz |  | IMAIN FUSE (Minimum Fuse Rating): | [8 empty] | 100.1247 |  |  | amps |  |  | Capacitance (per can): | 20.4706 | µF | [5 empty] | 3.8 | 0.0001-6.820215i | 0.000001-0.284176i | 0.010799+4.103496i | 10.798674+0.0001i |  | 0.0108+3.81932i | 0.116244+41.243593i | 10.809474+3.81942i | 1.208095+3.388636i | 1.208195-3.431579i | 3.8 | 3.6381
|  |  | f (System Frequency): | [10 empty] | 60 |  | (HZ) | [10 empty] | IRATED FUNDAMENTAL: | 278.1241 |  |  | amps |  | VCAP MAIN FUNDAMENTAL VOLTAGE: | [8 empty] | 7.2081 |  |  | kV | [10 empty] | 4 | 0.0001-6.479204i | 0.000001-0.269967i | 0.010799+4.319469i | 10.798674+0.0001i |  | 0.0108+4.049502i | 0.116221+43.729253i | 10.809474+4.049602i | 1.338464+3.544021i | 1.338564-2.935183i | 4 | 3.226
| DF (Damping Factor of High-Pass Filter): | [12 empty] | 2 | [12 empty] | IFILTER RMS CURRENT: | 314.8858 |  |  | amps |  | VCAP MAIN RMS VOLTAGE: | [8 empty] | 7.2345 |  |  | kV | [10 empty] | 4.2 | 0.0001-6.170671i | 0.000001-0.257111i | 0.010799+4.535443i | 10.798674+0.0001i |  | 0.0108+4.278332i | 0.116198+46.200314i | 10.809474+4.278432i | 1.471856+3.691491i | 1.471956-2.47918i | 4.2 | 2.8832
[33 empty] | VCAP MAIN, PEAK CAP VOLTAGE: | [8 empty] | 11.7418 |  |  | kV | [10 empty] | 4.4 | 0.0001-5.890186i | 0.000001-0.245424i | 0.010799+4.751416i | 10.798674+0.0001i |  | 0.0108+4.505992i | 0.116175+48.65874i | 10.809474+4.506092i | 1.607854+3.831232i | 1.607954-2.058954i | 4.4 | 2.6124
| Expected Harmonic Current (amps) Into Line Side of Filter of Filter Branch/Stage | [31 empty] | IMAIN CAP RMS CURRENT: | [8 empty] | 62.9772 |  |  | amps | [10 empty] | 4.6 | 0.0001-5.634091i | 0.000001-0.234754i | 0.010799+4.96739i | 10.798674+0.0001i |  | 0.0108+4.732636i | 0.116152+51.106194i | 10.809474+4.732736i | 1.746061+3.963426i | 1.746161-1.670665i | 4.6 | 2.4167
| (n) Harmonic: | [5 empty] | 1 | 2 |  | 3 |  | 4 | 5 |  | 7 | 11 |  | 13 | 17 | 19 |  | 23 |  | 25 | 29 |  | 31 |  | 35 |  | 37 |  | QMAIN CAPACITOR (1-phase): | [8 empty] | 2091.6563 |  |  | kvar | [10 empty] | 4.8 | 0.0001-5.399337i | 0.000001-0.224972i | 0.010799+5.183363i | 10.798674+0.0001i |  | 0.0108+4.958391i | 0.11613+53.544049i | 10.809474+4.958491i | 1.886095+4.088253i | 1.886195-1.311084i | 4.8 | 2.2971
| (In) Filter current: | [5 empty] | 278.1241 | 0 |  | 0 |  | 0 | 100 |  | 80 | 60 |  | 30 | 20 | 10 |  | 10 |  | 10 | 0 |  | 0 |  | 10 |  | 10 | [24 empty] | 5 | 0.0001-5.183363i | 0.000001-0.215973i | 0.010799+5.399337i | 10.798674+0.0001i |  | 0.0108+5.183364i | 0.116107+55.973459i | 10.809474+5.183464i | 2.027593+4.205894i | 2.027693-0.977469i | 5 | 2.251
[33 empty] | Auxiliary Capacitor Group Design Ratings Versus Duty Rating | [22 empty] | 5.2 | 0.0001-4.984003i | 0.000001-0.207667i | 0.010799+5.61531i | 10.798674+0.0001i |  | 0.0108+5.407643i | 0.116085+58.395375i | 10.809474+5.407743i | 2.170206+4.316534i | 2.170306-0.667469i | 5.2 | 2.2706
| Main Capacitor Group Rating Details | [38 empty] | Design Values | [15 empty] | 5.4 | 0.0001-4.79941i | 0.000001-0.199975i | 0.010799+5.831284i | 10.798674+0.0001i |  | 0.0108+5.631309i | 0.116063+60.810671i | 10.809474+5.631409i | 2.313612+4.420361i | 2.313712-0.379049i | 5.4 | 2.3446
VCAP MAIN RATING (Voltage Rating of Main Capacitor): | [13 empty] | 9.96 |  | kV | [9 empty] | Individual Capacitor Rating: | 765.5385 |  |  | kvar | [9 empty] | At Nominal Voltage | [5 empty] | At Nominal 110% System Voltage | [9 empty] | 5.6 | 0.0001-4.628003i | 0.000001-0.192833i | 0.010799+6.047257i | 10.798674+0.0001i |  | 0.0108+5.854424i | 0.11604+63.220017i | 10.809474+5.854524i | 2.457497+4.517569i | 2.457597-0.110434i | 5.6 | 2.4601
NMAIN (Number of Main Capacitors Per Phase): | [13 empty] | 5 | [11 empty] | QMAIN RATED PER PHASE: | 3827.6923 |  |  | kvar |  |  |  | Design Parameter | [12 empty] | Rated Duty | [8 empty] | 5.8 | 0.0001-4.468417i | 0.000001-0.186184i | 0.010799+6.263231i | 10.798674+0.0001i |  | 0.0108+6.077047i | 0.116018+65.624051i | 10.809474+6.077147i | 2.601576+4.608355i | 2.601676+0.139938i | 5.8 | 2.6054
[7 empty] | HD- Heavy Duty Capacitor | [18 empty] | XC-MAIN: | 25.9168 |  |  | Ohms | [7 empty] | % RATED VOLTS: |  | 30.12% | [5 empty] | 33.11% | 125% | [8 empty] | 6 | 0.0001-4.319469i | 0.000001-0.179978i | 0.010799+6.479204i | 10.798674+0.0001i |  | 0.0108+6.299226i | 0.115996+68.023289i | 10.809474+6.299326i | 2.745576+4.692921i | 2.745676+0.373452i | 6 | 2.771
[26 empty] | Main Cap Capacitance (per phase): | 102.35 |  |  | 𝜇F/Phase | [7 empty] | % CREST VOLTAGE: |  | 33.69% | [5 empty] | 43.69% | 135% | [8 empty] | 6.2 | 0.0001-4.180132i | 0.000001-0.174172i | 0.010799+6.695178i | 10.798674+0.0001i |  | 0.0108+6.521006i | 0.115974+70.418219i | 10.809474+6.521106i | 2.889249+4.771474i | 2.889349+0.591342i | 6.2 | 2.9492
| Auxiliary Capacitor Group Rating Details | [36 empty] | % 60HZ AMPS: |  | 32.75% | [5 empty] | 35.53% | 135% | [8 empty] | 6.4 | 0.0001-4.049503i | 0.000001-0.168729i | 0.010799+6.911151i | 10.798674+0.0001i |  | 0.0108+6.742422i | 0.115951+72.809218i | 10.809474+6.742522i | 3.032359+4.84422i | 3.032459+0.794717i | 6.4 | 3.1349
[38 empty] | % 60HZ KVAR: |  | 9.304% | [5 empty] | 11.2% | 135% | [8 empty] | 6.6 | 0.0001-3.92679i | 0.000001-0.163616i | 0.010799+7.127125i | 10.798674+0.0001i |  | 0.0108+6.963509i | 0.115929+75.196665i | 10.809474+6.963609i | 3.174696+4.91137i | 3.174796+0.98458i | 6.6 | 3.324
| VCAP AUX RATING (Voltage Rating of Aux Capacitor): | [12 empty] | 1 |  | kV | [9 empty] | Individual Capacitor Rating: | 154.3399 |  |  | kvar | [25 empty] | 6.8 | 0.0001-3.811297i | 0.000001-0.158804i | 0.010799+7.343098i | 10.798674+0.0001i |  | 0.0108+7.184294i | 0.115907+77.58085i | 10.809474+7.184394i | 3.31606+4.973135i | 3.31616+1.161838i | 6.8 | 3.5138
NAUX (Number of Auxiliary Capacitors Per Phase): | [13 empty] | 6 | [11 empty] | QAUX RATED PER PHASE: | 926.0397 |  |  | kvar |  |  | ICAP AUX (Fundamental Amps Each Aux Capacitor): | [8 empty] | 46.354 |  |  | amps | [10 empty] | 7 | 0.0001-3.702402i | 0.000001-0.154267i | 0.010799+7.559072i | 10.798674+0.0001i |  | 0.0108+7.404805i | 0.115885+79.962076i | 10.809474+7.404905i | 3.456276+5.029725i | 3.456376+1.327323i | 7 | 3.7025
[7 empty] | HD- Heavy Duty Capacitor | [18 empty] | XC-AUX: | 1.0799 |  |  | Ohms |  |  | IAUX FUSE (Minimum Fuse Rating): | [8 empty] | 83.4372 |  |  | amps |  |  | Capacitive Reactance (per can): | 6.4792 | Ohms | [5 empty] | 7.2 | 0.0001-3.599558i | 0.000001-0.149982i | 0.010799+7.775045i | 10.798674+0.0001i |  | 0.0108+7.625063i | 0.115863+82.340571i | 10.809474+7.625163i | 3.59518+5.081352i | 3.59528+1.481794i | 7.2 | 3.8887
[26 empty] | Aux Cap Capacitance (per phase): | 2456.47 |  |  | 𝜇F/Phase |  |  | VCAP AUX FUNDAMENTAL VOLTAGE: | [8 empty] | 0.30034 |  |  | kV |  |  | Capacitance (per can): | 409.4115 | µf | [5 empty] | 7.4 | 0.0001-3.502273i | 0.000001-0.145928i | 0.010799+7.991018i | 10.798674+0.0001i |  | 0.0108+7.84509i | 0.115841+84.71657i | 10.809474+7.84519i | 3.732627+5.128224i | 3.732727+1.625951i | 7.4 | 4.0715
| Tuning Reactor | [31 empty] | VCAP AUX RMS VOLTAGE: | [8 empty] | 0.30117 |  |  | kV | [10 empty] | 7.6 | 0.0001-3.410107i | 0.000001-0.142088i | 0.010799+8.206992i | 10.798674+0.0001i |  | 0.0108+8.064904i | 0.115819+87.09027i | 10.809474+8.065004i | 3.868487+5.170548i | 3.868587+1.760441i | 7.6 | 4.2503
| X/Rratio (Tuning Reactor at System Frequency): | [12 empty] | 100 |  |  | XL (Inductive Reactance): | [9 empty] | 1.0799 |  |  | ohms |  |  | VCAP AUX PEAK CAP VOLTAGE: | [8 empty] | 0.47639 |  |  | kV | [10 empty] | 7.8 | 0.0001-3.322669i | 0.000001-0.138445i | 0.010799+8.422965i | 10.798674+0.0001i |  | 0.0108+8.28452i | 0.115797+89.461832i | 10.809474+8.28462i | 4.002644+5.208528i | 4.002744+1.885859i | 7.8 | 4.4248
[13 empty] | Enter Fundamental Current Design Margin: | 1.5 |  | HL (Inductance): | [10 empty] | 2.8645 |  |  | mH |  |  | ICAP AUX RMS CURRENT: | [8 empty] | 50.548 |  |  | amps | [10 empty] | 8 | 0.0001-3.239602i | 0.000001-0.134983i | 0.010799+8.638939i | 10.798674+0.0001i |  | 0.0108+8.503956i | 0.115775+91.83145i | 10.809474+8.504056i | 4.134997+5.242365i | 4.135097+2.002763i | 8 | 4.5946
[13 empty] | Enter Harmonic Current Design Margin: | 1.5 | [18 empty] | QAUX CAPACITOR (1-phase): | [8 empty] | 86.1568 |  |  | kvar | [10 empty] | 8.2 | 0.0001-3.160587i | 0.000001-0.131691i | 0.010799+8.854912i | 10.798674+0.0001i |  | 0.0108+8.723221i | 0.115753+94.199221i | 10.809474+8.723321i | 4.265454+5.272254i | 4.265554+2.111667i | 8.2 | 4.7596
High-Pass Resistor
[13 empty] | Rw (Resistor KW/Phase - Specified): | 100 |  | kW/Phase | [39 empty] | 8.4 | 0.0001-3.085335i | 0.000001-0.128556i | 0.010799+9.070886i | 10.798674+0.0001i |  | 0.0108+8.94233i | 0.115731+96.565308i | 10.809474+8.94243i | 4.393942+5.298388i | 4.394042+2.213053i | 8.4 | 4.9199
[10 empty] | Ifundamental resistor current (actual): | 0 |  | amps | [12 empty] | R (Resistor Ohm rating/phase): | 10.7987 |  |  | Ohms | [25 empty] | 8.6 | 0.0001-3.013583i | 0.000001-0.125566i | 0.010799+9.286859i | 10.798674+0.0001i |  | 0.0108+9.161293i | 0.11571+98.929818i | 10.809474+9.161393i | 4.520393+5.320955i | 4.520493+2.307372i | 8.6 | 5.0753
[10 empty] | Ifundamental resistor current (specified): | 96.231 |  | amps | [12 empty] | (Rw) (Resistor KW/phase, actual): | 77.4187 |  |  | kW/Phase | [25 empty] | 8.8 | 0.0001-2.945093i | 0.000001-0.122712i | 0.010799+9.502833i | 10.798674+0.0001i |  | 0.0108+9.380121i | 0.115688+101.29287i | 10.809474+9.380221i | 4.644753+5.340136i | 4.644853+2.395043i | 8.8 | 5.226
|  | Info@VarStec.com | [29 empty] | Rev Date: 4-19-2026 |  | Info@VarStec.com | [16 empty] | 2 ¦ P a g e |  |  |  |  | 9 | 0.0001-2.879646i | 0.000001-0.119985i | 0.010799+9.718806i | 10.798674+0.0001i |  | 0.0108+9.598821i | 0.115666+103.65454i | 10.809474+9.598921i | 4.766977+5.356107i | 4.767077+2.476461i | 9 | 5.372
[56 empty] | 9.2 | 0.0001-2.817045i | 0.000001-0.117377i | 0.010799+9.93478i | 10.798674+0.0001i |  | 0.0108+9.817403i | 0.115644+106.014936i | 10.809474+9.817503i | 4.88703+5.369041i | 4.88713+2.551996i | 9.2 | 5.5133
[56 empty] | 9.4 | 0.0001-2.757108i | 0.000001-0.11488i | 0.010799+10.150753i | 10.798674+0.0001i |  | 0.0108+10.035873i | 0.115622+108.374122i | 10.809474+10.035973i | 5.004882+5.379102i | 5.004982+2.621994i | 9.4 | 5.6502
[56 empty] | 9.6 | 0.0001-2.699668i | 0.000001-0.112486i | 0.010799+10.366727i | 10.798674+0.0001i |  | 0.0108+10.254241i | 0.1156+110.732207i | 10.809474+10.254341i | 5.120516+5.386449i | 5.120616+2.686781i | 9.6 | 5.7827
[56 empty] | 9.8 | 0.0001-2.644573i | 0.000001-0.110191i | 0.010799+10.5827i | 10.798674+0.0001i |  | 0.0108+10.472509i | 0.115578+113.089212i | 10.809474+10.472609i | 5.233918+5.391237i | 5.234018+2.746664i | 9.8 | 5.9109
[56 empty] | 10 | 0.0001-2.591682i | 0.000001-0.107987i | 0.010799+10.798674i | 10.798674+0.0001i |  | 0.0108+10.690687i | 0.115557+115.445245i | 10.809474+10.690787i | 5.345082+5.393613i | 5.345182+2.801931i | 10 | 6.035
| Enter Customer PO # ¦ Stage 1 | [31 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 10.2 | 0.0001-2.540864i | 0.000001-0.105869i | 0.010799+11.014647i | 10.798674+0.0001i |  | 0.0108+10.908778i | 0.115535+117.800338i | 10.809474+10.908878i | 5.454006+5.393717i | 5.454106+2.852853i | 10.2 | 6.1552
[56 empty] | 10.4 | 0.0001-2.492002i | 0.000001-0.103833i | 0.010799+11.230621i | 10.798674+0.0001i |  | 0.0108+11.126788i | 0.115513+120.154557i | 10.809474+11.126888i | 5.560697+5.391687i | 5.560797+2.899685i | 10.4 | 6.2714
| Table of Currents and Voltages | [31 empty] | 📐 SIMPLIFIED ONE-LINE DIAGRAM | [18 empty] | (In) Filter Current | (In) Filter Current | Calculated Reactor Current | VarStec Reactor Rating | 10.6 | 0.0001-2.444983i | 0.000001-0.101874i | 0.010799+11.446594i | 10.798674+0.0001i |  | 0.0108+11.34472i | 0.115491+122.507934i | 10.809474+11.34482i | 5.665163+5.387652i | 5.665263+2.942669i | 10.6 | 6.3839
[18 empty] | Iaux Capacitor and IREACTOR CURRENT (amps) | [37 empty] | 10.8 | 0.0001-2.399705i | 0.000001-0.099988i | 0.010799+11.662568i | 10.798674+0.0001i |  | 0.0108+11.56258i | 0.115469+124.860533i | 10.809474+11.56268i | 5.767418+5.381735i | 5.767518+2.98203i | 10.8 | 6.4928
[6 empty] | (In) Filter Current (amps): |  |  |  | VCAP MAIN Voltage (volts) |  |  |  | VCAP AUX Voltage (volts) | [18 empty] | 12.47kV, 60Hz C-High-Pass Filter, Wye-Connected | [22 empty] | 11 | 0.0001-2.356074i | 0.000001-0.09817i | 0.010799+11.878541i | 10.798674+0.0001i |  | 0.0108+11.780371i | 0.115448+127.212387i | 10.809474+11.780471i | 5.867479+5.374056i | 5.867579+3.017982i | 11 | 6.5982
| Harmonic #: (n) | [20 empty] | IRESISTOR CURRENT (amps) |  |  |  |  | Voltage Distortion* | [5 empty] | 6,000 Kvar 3-Phase, 5.0 Tuning | [22 empty] | 11.2 | 0.0001-2.314001i | 0.000001-0.096417i | 0.010799+12.094514i | 10.798674+0.0001i |  | 0.0108+11.998097i | 0.115426+129.563539i | 10.809474+11.998197i | 5.965368+5.364728i | 5.965468+3.050727i | 11.2 | 6.7003
[52 empty] | 1 | 278.1241 | 278.1241 | 417.1862 | 11.4 | 0.0001-2.273405i | 0.000001-0.094725i | 0.010799+12.310488i | 10.798674+0.0001i |  | 0.0108+12.215763i | 0.115404+131.914043i | 10.809474+12.215863i | 6.061108+5.353857i | 6.061208+3.080452i | 11.4 | 6.7991
| 1 |  |  |  |  | 278.1241 |  |  |  | 7208.0925 |  |  |  | 300.3372 |  |  |  | 278.1241 |  |  |  | 0 |  |  |  |  | 100.1% | [15 empty] | Fundamental Current 278.1 amps/phase | [8 empty] | 2 | 0 | 0 | 0 | 11.6 | 0.0001-2.234208i | 0.000001-0.093092i | 0.010799+12.526461i | 10.798674+0.0001i |  | 0.0108+12.433369i | 0.115382+134.2639i | 10.809474+12.433469i | 6.154725+5.341547i | 6.154825+3.107339i | 11.6 | 6.8947
| 2 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0% | [15 empty] | RMS current 314.89 amps/phase | [8 empty] | 3 | 0 | 0 | 0 | 11.8 | 0.0001-2.19634i | 0.000001-0.091514i | 0.010799+12.742435i | 10.798674+0.0001i |  | 0.0108+12.650921i | 0.115361+136.613173i | 10.809474+12.651021i | 6.246249+5.327895i | 6.246349+3.131555i | 11.8 | 6.9874
| 3 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0% | [24 empty] | 4 | 0 | 0 | 0 | 12 | 0.0001-2.159735i | 0.000001-0.089989i | 0.010799+12.958408i | 10.798674+0.0001i |  | 0.0108+12.868419i | 0.115339+138.961863i | 10.809474+12.868519i | 6.33571+5.312993i | 6.33581+3.153258i | 12 | 7.0771
| 4 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0% | [15 empty] | Reactor: 1.08 ohms, 2.86 mH | [8 empty] | 5 | 100 | 90.1523 | 135.2285 | 12.2 | 0.0001-2.124329i | 0.000001-0.088514i | 0.010799+13.174382i | 10.798674+0.0001i |  | 0.0108+13.085868i | 0.115317+141.310024i | 10.809474+13.085968i | 6.42314+5.296929i | 6.42324+3.1726i | 12.2 | 7.164
| 5 |  |  |  |  | 100 |  |  |  | 518.3363 |  |  |  | 19.4705 |  |  |  | 90.1523 |  |  |  | 43.2731 |  |  |  |  | 3.127% | [11 empty] | High-Pass Resistor: 10.8 ohms/Phase |  |  |  | I1= 278.1 amps nominal | [8 empty] | 7 | 80 | 65.9783 | 98.9675 | 12.4 | 0.0001-2.090066i | 0.000001-0.087086i | 0.010799+13.390355i | 10.798674+0.0001i |  | 0.0108+13.303269i | 0.115295+143.657666i | 10.809474+13.303369i | 6.508573+5.279787i | 6.508673+3.189721i | 12.4 | 7.2483
| 7 |  |  |  |  | 80 |  |  |  | 296.1922 |  |  |  | 10.1783 |  |  |  | 65.9783 |  |  |  | 45.2423 |  |  |  |  | 4.114% | [11 empty] | 77 KW/Phase | [12 empty] | 11 | 60 | 40.5435 | 60.8152 | 12.6 | 0.0001-2.05689i | 0.000001-0.085704i | 0.010799+13.606329i | 10.798674+0.0001i |  | 0.0108+13.520625i | 0.115274+146.004823i | 10.809474+13.520725i | 6.592044+5.261645i | 6.592144+3.204755i | 12.6 | 7.3299
| 11 |  |  |  |  | 60 |  |  |  | 141.3645 |  |  |  | 3.9801 |  |  |  | 40.5435 |  |  |  | 44.2292 |  |  |  |  | 5.499% | [11 empty] | 84.7 RMS Amps | [12 empty] | 13 | 30 | 18.3595 | 27.5392 | 12.8 | 0.0001-2.024751i | 0.000001-0.084365i | 0.010799+13.822302i | 10.798674+0.0001i |  | 0.0108+13.737937i | 0.115252+148.351504i | 10.809474+13.738037i | 6.673588+5.242578i | 6.673688+3.217827i | 12.8 | 7.4089
| 13 |  |  |  |  | 30 |  |  |  | 59.808 |  |  |  | 1.5251 |  |  |  | 18.3595 |  |  |  | 23.7261 |  |  |  |  | 3.119% | [15 empty] | Aux Capacitor: Qty(18), 154 kvar, 1 kV, 409.41 µF/Can | [8 empty] | 17 | 20 | 10.1665 | 15.2498 | 13 | 0.0001-1.993601i | 0.000001-0.083067i | 0.010799+14.038276i | 10.798674+0.0001i |  | 0.0108+13.955209i | 0.11523+150.697754i | 10.809474+13.955309i | 6.753243+5.222656i | 6.753343+3.229055i | 13 | 7.4856
| 17 |  |  |  |  | 20 |  |  |  | 30.4904 |  |  |  | 0.64579 |  |  |  | 10.1665 |  |  |  | 17.2233 |  |  |  |  | 2.395% | [15 empty] | Optional Fuse: 83 (Minimum Amps) | [8 empty] | 19 | 10 | 4.6676 | 7.0014 | 13.2 | 0.0001-1.963395i | 0.000001-0.081808i | 0.010799+14.254249i | 10.798674+0.0001i |  | 0.0108+14.172441i | 0.115208+153.043571i | 10.809474+14.172541i | 6.831045+5.201946i | 6.831145+3.238551i | 13.2 | 7.5599
| 19 |  |  |  |  | 10 |  |  |  | 13.6404 |  |  |  | 0.26528 |  |  |  | 4.6676 |  |  |  | 8.8438 |  |  |  |  | 1.249% | [24 empty] | 23 | 10 | 3.9936 | 5.9904
| 23 |  |  |  |  | 10 |  |  |  | 11.2682 |  |  |  | 0.1875 |  |  |  | 3.9936 |  |  |  | 9.1679 |  |  |  |  | 1.32% | [24 empty] | 25 | 10 | 3.719 | 5.5786 | 13.4 | 0.0001-1.934091i | 0.000001-0.080587i | 0.010799+14.470223i | 10.798674+0.0001i |  | 0.0108+14.389636i | 0.115187+155.388989i | 10.809474+14.389736i | 6.907033+5.180512i | 6.907133+3.246421i | 13.4 | 7.632
| 25 |  |  |  |  | 10 |  |  |  | 10.3667 |  |  |  | 0.16064 |  |  |  | 3.719 |  |  |  | 9.2827 |  |  |  |  | 1.345% | [15 empty] | Capacitor Fuse: 100 (Minimum Amps) | [8 empty] | 29 | 0 | 0 | 0 | 13.6 | 0.0001-1.905648i | 0.000001-0.079402i | 0.010799+14.686196i | 10.798674+0.0001i |  | 0.0108+14.606794i | 0.115165+157.734008i | 10.809474+14.606894i | 6.981243+5.158413i | 6.981343+3.252765i | 13.6 | 7.7019
| 29 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0% | [24 empty] | 31 | 0 | 0 | 0 | 13.8 | 0.0001-1.87803i | 0.000001-0.078251i | 0.010799+14.90217i | 10.798674+0.0001i |  | 0.0108+14.823919i | 0.115143+160.07867i | 10.809474+14.824019i | 7.053714+5.135706i | 7.053814+3.257676i | 13.8 | 7.7697
| 31 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0% | [24 empty] | 35 | 10 | 2.7493 | 4.1239 | 14 | 0.0001-1.851201i | 0.000001-0.077133i | 0.010799+15.118143i | 10.798674+0.0001i |  | 0.0108+15.04101i | 0.115122+162.422965i | 10.809474+15.04111i | 7.124484+5.112442i | 7.124584+3.261241i | 14 | 7.8355
| 35 |  |  |  |  | 10 |  |  |  | 7.4048 |  |  |  | 0.084825 |  |  |  | 2.7493 |  |  |  | 9.6146 |  |  |  |  | 1.417% | [15 empty] | Main Capacitor: Qty(15), 766 kvar, 9.96 kV, 20.47 µF/Can | [8 empty] | 37 | 10 | 2.6109 | 3.9163 | 14.2 | 0.0001-1.825128i | 0.000001-0.076047i | 0.010799+15.334117i | 10.798674+0.0001i |  | 0.0108+15.25807i | 0.1151+164.766925i | 10.809474+15.25817i | 7.193592+5.088673i | 7.193692+3.263545i | 14.2 | 7.8994
| 37 |  |  |  |  | 10 |  |  |  | 7.0045 |  |  |  | 0.0762 |  |  |  | 2.6109 |  |  |  | 9.6532 |  |  |  |  | 1.425% | [28 empty] | 14.4 | 0.0001-1.799779i | 0.000001-0.074991i | 0.010799+15.55009i | 10.798674+0.0001i |  | 0.0108+15.475099i | 0.115078+167.11055i | 10.809474+15.475199i | 7.261073+5.064446i | 7.261173+3.264667i | 14.4 | 7.9613
[5 empty] | RMS | 314.8858 |  |  |  | 7234.5017 |  |  |  | 301.1708 |  |  |  | 303.2882 |  |  |  | 84.6716 |  |  |  |  | Vthd: 9.03% | [28 empty] | 14.6 | 0.0001-1.775124i | 0.000001-0.073964i | 0.010799+15.766063i | 10.798674+0.0001i |  | 0.0108+15.692099i | 0.115056+169.453863i | 10.809474+15.692199i | 7.326967+5.039804i | 7.327067+3.26468i | 14.6 | 8.0215
| * Voltage distortion at filter incoming based on specified harmonic currents in rows 24 and 25 of page 1. | [54 empty] | 14.8 | 0.0001-1.751136i | 0.000001-0.072964i | 0.010799+15.982037i | 10.798674+0.0001i |  | 0.0108+15.909073i | 0.115035+171.796894i | 10.809474+15.909173i | 7.391312+5.01479i | 7.391412+3.263654i | 14.8 | 8.0799
[56 empty] | 15 | 0.0001-1.727788i | 0.000001-0.071991i | 0.010799+16.19801i | 10.798674+0.0001i |  | 0.0108+16.126019i | 0.115013+174.139623i | 10.809474+16.126119i | 7.454142+4.989442i | 7.454242+3.261654i | 15 | 8.1366
[56 empty] | 15.2 | 0.0001-1.705054i | 0.000001-0.071044i | 0.010799+16.413984i | 10.798674+0.0001i |  | 0.0108+16.34294i | 0.114991+176.482082i | 10.809474+16.34304i | 7.515495+4.963798i | 7.515595+3.258744i | 15.2 | 8.1917
[56 empty] | 15.4 | 0.0001-1.68291i | 0.000001-0.070121i | 0.010799+16.629957i | 10.798674+0.0001i |  | 0.0108+16.559836i | 0.11497+178.824272i | 10.809474+16.559936i | 7.575407+4.937893i | 7.575507+3.254983i | 15.4 | 8.2452
[56 empty] | 15.6 | 0.0001-1.661334i | 0.000001-0.069222i | 0.010799+16.845931i | 10.798674+0.0001i |  | 0.0108+16.776709i | 0.114948+181.166212i | 10.809474+16.776809i | 7.633912+4.911758i | 7.634012+3.250424i | 15.6 | 8.2972
[56 empty] | 15.8 | 0.0001-1.640305i | 0.000001-0.068346i | 0.010799+17.061904i | 10.798674+0.0001i |  | 0.0108+16.993558i | 0.114926+183.507894i | 10.809474+16.993658i | 7.691047+4.885425i | 7.691147+3.24512i | 15.8 | 8.3477
[56 empty] | 16 | 0.0001-1.619801i | 0.000001-0.067492i | 0.010799+17.277878i | 10.798674+0.0001i |  | 0.0108+17.210386i | 0.114905+185.849349i | 10.809474+17.210486i | 7.746844+4.858922i | 7.746944+3.239121i | 16 | 8.3968
[56 empty] | 16.2 | 0.0001-1.599803i | 0.000001-0.066658i | 0.010799+17.493851i | 10.798674+0.0001i |  | 0.0108+17.427193i | 0.114883+188.190577i | 10.809474+17.427293i | 7.801339+4.832276i | 7.801439+3.232473i | 16.2 | 8.4446
[56 empty] | 16.4 | 0.0001-1.580294i | 0.000001-0.065846i | 0.010799+17.709825i | 10.798674+0.0001i |  | 0.0108+17.643979i | 0.114861+190.531578i | 10.809474+17.644079i | 7.854563+4.805512i | 7.854663+3.225218i | 16.4 | 8.491
[56 empty] | 16.6 | 0.0001-1.561254i | 0.000001-0.065052i | 0.010799+17.925798i | 10.798674+0.0001i |  | 0.0108+17.860746i | 0.11484+192.872375i | 10.809474+17.860846i | 7.906549+4.778653i | 7.906649+3.217399i | 16.6 | 8.5362
[56 empty] | 16.8 | 0.0001-1.542668i | 0.000001-0.064278i | 0.010799+18.141772i | 10.798674+0.0001i |  | 0.0108+18.077494i | 0.114818+195.212966i | 10.809474+18.077594i | 7.957328+4.751723i | 7.957428+3.209055i | 16.8 | 8.5801
[56 empty] | 17 | 0.0001-1.524519i | 0.000001-0.063522i | 0.010799+18.357745i | 10.798674+0.0001i |  | 0.0108+18.294223i | 0.114796+197.553351i | 10.809474+18.294323i | 8.006932+4.72474i | 8.007032+3.200221i | 17 | 8.6229
[56 empty] | 17.2 | 0.0001-1.506792i | 0.000001-0.062783i | 0.010799+18.573719i | 10.798674+0.0001i |  | 0.0108+18.510936i | 0.114775+199.893564i | 10.809474+18.511036i | 8.055391+4.697725i | 8.055491+3.190933i | 17.2 | 8.6645
[56 empty] | 17.4 | 0.0001-1.489472i | 0.000001-0.062061i | 0.010799+18.789692i | 10.798674+0.0001i |  | 0.0108+18.727631i | 0.114753+202.233583i | 10.809474+18.727731i | 8.102734+4.670696i | 8.102834+3.181224i | 17.4 | 8.7049
[56 empty] | 17.6 | 0.0001-1.472546i | 0.000001-0.061356i | 0.010799+19.005666i | 10.798674+0.0001i |  | 0.0108+18.94431i | 0.114731+204.573429i | 10.809474+18.94441i | 8.14899+4.643669i | 8.14909+3.171123i | 17.6 | 8.7444
[56 empty] | 17.8 | 0.0001-1.456001i | 0.000001-0.060667i | 0.010799+19.221639i | 10.798674+0.0001i |  | 0.0108+19.160972i | 0.11471+206.913091i | 10.809474+19.161072i | 8.194188+4.61666i | 8.194288+3.160659i | 17.8 | 8.7827
[56 empty] | 18 | 0.0001-1.439823i | 0.000001-0.059993i | 0.010799+19.437613i | 10.798674+0.0001i |  | 0.0108+19.37762i | 0.114688+209.252602i | 10.809474+19.37772i | 8.238355+4.589683i | 8.238455+3.14986i | 18 | 8.8201
[56 empty] | 18.2 | 0.0001-1.424001i | 0.000001-0.059333i | 0.010799+19.653586i | 10.798674+0.0001i |  | 0.0108+19.594253i | 0.114666+211.591952i | 10.809474+19.594353i | 8.281518+4.562753i | 8.281618+3.138752i | 18.2 | 8.8565
[56 empty] | 18.4 | 0.0001-1.408523i | 0.000001-0.058688i | 0.010799+19.869559i | 10.798674+0.0001i |  | 0.0108+19.810871i | 0.114645+213.931139i | 10.809474+19.810971i | 8.323704+4.535881i | 8.323804+3.127358i | 18.4 | 8.8919
|  | Info@VarStec.com | [29 empty] | 3 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 4 ¦ P a g e |  |  |  |  | 18.6 | 0.0001-1.393377i | 0.000001-0.058057i | 0.010799+20.085533i | 10.798674+0.0001i |  | 0.0108+20.027476i | 0.114623+216.270185i | 10.809474+20.027576i | 8.364937+4.50908i | 8.365037+3.115703i | 18.6 | 8.9264
[56 empty] | 18.8 | 0.0001-1.378554i | 0.000001-0.05744i | 0.010799+20.301506i | 10.798674+0.0001i |  | 0.0108+20.244066i | 0.114601+218.60907i | 10.809474+20.244166i | 8.405242+4.48236i | 8.405342+3.103806i | 18.8 | 8.9601
[56 empty] | 19 | 0.0001-1.364043i | 0.000001-0.056835i | 0.010799+20.51748i | 10.798674+0.0001i |  | 0.0108+20.460645i | 0.11458+220.947836i | 10.809474+20.460745i | 8.444645+4.455732i | 8.444745+3.091689i | 19 | 8.9929
[56 empty] | 19.2 | 0.0001-1.349834i | 0.000001-0.056243i | 0.010799+20.733453i | 10.798674+0.0001i |  | 0.0108+20.67721i | 0.114558+223.286451i | 10.809474+20.67731i | 8.483168+4.429204i | 8.483268+3.07937i | 19.2 | 9.0249 | [6 empty] | 417.1862 | 174044.3405
[56 empty] | 19.4 | 0.0001-1.335918i | 0.000001-0.055663i | 0.010799+20.949427i | 10.798674+0.0001i |  | 0.0108+20.893764i | 0.114536+225.624947i | 10.809474+20.893864i | 8.520834+4.402785i | 8.520934+3.066867i | 19.4 | 9.056 | [6 empty] | 0 | 0
[56 empty] | 19.6 | 0.0001-1.322287i | 0.000001-0.055095i | 0.010799+21.1654i | 10.798674+0.0001i |  | 0.0108+21.110305i | 0.114515+227.963303i | 10.809474+21.110405i | 8.557667+4.376484i | 8.557767+3.054197i | 19.6 | 9.0864 | [6 empty] | 0 | 0
| Enter Customer PO # ¦ Stage 1 | [31 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 19.8 | 0.0001-1.30893i | 0.000001-0.054539i | 0.010799+21.381374i | 10.798674+0.0001i |  | 0.0108+21.326835i | 0.114493+230.30154i | 10.809474+21.326935i | 8.593687+4.350308i | 8.593787+3.041378i | 19.8 | 9.1161 | [6 empty] | 0 | 0
[56 empty] | 20 | 0.0001-1.295841i | 0.000001-0.053993i | 0.010799+21.597347i | 10.798674+0.0001i |  | 0.0108+21.543354i | 0.114471+232.639658i | 10.809474+21.543454i | 8.628916+4.324263i | 8.629016+3.028422i | 20 | 9.145 | [6 empty] | 135.2285 | 18286.736
| 🧮 VENDOR SPECIFICATIONS | [31 empty] | 🧮 3-PHASE LOSS ESTIMATES | [22 empty] | 20.2 | 0.0001-1.283011i | 0.000001-0.053459i | 0.010799+21.813321i | 10.798674+0.0001i |  | 0.0108+21.759862i | 0.11445+234.977657i | 10.809474+21.759962i | 8.663374+4.298356i | 8.663474+3.015345i | 20.2 | 9.1732 | [6 empty] | 98.9675 | 9794.5586
|  | Reactor Specification | [53 empty] | 20.4 | 0.0001-1.270432i | 0.000001-0.052935i | 0.010799+22.029294i | 10.798674+0.0001i |  | 0.0108+21.976359i | 0.114428+237.315538i | 10.809474+21.976459i | 8.697082+4.272592i | 8.697182+3.00216i | 20.4 | 9.2008 | [6 empty] | 60.8152 | 3698.4906
[33 empty] | 60 Hertz Losses | [22 empty] | 20.6 | 0.0001-1.258098i | 0.000001-0.052421i | 0.010799+22.245268i | 10.798674+0.0001i |  | 0.0108+22.192847i | 0.114406+239.653321i | 10.809474+22.192947i | 8.730059+4.246977i | 8.730159+2.988879i | 20.6 | 9.2276 | [6 empty] | 27.5392 | 758.4102
|  |  |  | Filter Type: | C-High-Pass | [11 empty] | Return Quote to: | VarStec Power Solutions | [15 empty] | Main Capacitor Losses: | [6 empty] | 1148.3077 |  |  | Watts, 3-Phase or 3918 BTUs/Hour | [11 empty] | 20.8 | 0.0001-1.246001i | 0.000001-0.051917i | 0.010799+22.461241i | 10.798674+0.0001i |  | 0.0108+22.409324i | 0.114385+241.990986i | 10.809474+22.409424i | 8.762324+4.221515i | 8.762424+2.975514i | 20.8 | 9.2539 | [6 empty] | 15.2498 | 232.5561
|  |  |  | Stage/Branch: | Stage 1 | [28 empty] | Main Capacitor Fuse Losses: | [6 empty] | 3033.5537 |  |  | Watts, 3-Phase or 10351 BTUs/Hour | [11 empty] | 21 | 0.0001-1.234134i | 0.000001-0.051422i | 0.010799+22.677215i | 10.798674+0.0001i |  | 0.0108+22.625793i | 0.114363+244.328564i | 10.809474+22.625893i | 8.793895+4.196211i | 8.793995+2.962077i | 21 | 9.2795 | [6 empty] | 7.0014 | 49.0193
|  |  |  | Tuning Point: | 5 | [28 empty] | Aux Capacitor Losses : | [6 empty] | 277.8119 |  |  | Watts, 3-Phase or 948 BTUs/Hour | [11 empty] | 21.2 | 0.0001-1.222491i | 0.000001-0.050937i | 0.010799+22.893188i | 10.798674+0.0001i |  | 0.0108+22.842251i | 0.114341+246.666023i | 10.809474+22.842351i | 8.824791+4.171068i | 8.824891+2.948577i | 21.2 | 9.3045 | [6 empty] | 5.9904 | 35.8851
[34 empty] | Aux Capacitor Fuse Losses: | [6 empty] | 3069.5537 |  |  | Watts, 3-Phase or 10474 BTUs/Hour | [11 empty] | 21.4 | 0.0001-1.211066i | 0.000001-0.050461i | 0.010799+23.109162i | 10.798674+0.0001i |  | 0.0108+23.058701i | 0.11432+249.003396i | 10.809474+23.058801i | 8.855028+4.146091i | 8.855128+2.935025i | 21.4 | 9.3289 | [6 empty] | 5.5786 | 31.1203
|  | Current Spectrum | [6 empty] | Tuning Reactor Details | [24 empty] | High-Pass Resistor Losses, 60 Hertz: | [6 empty] | 0 |  |  | Watts, 3-Phase or 0 BTUs/Hour | [11 empty] | 21.6 | 0.0001-1.199853i | 0.000001-0.049994i | 0.010799+23.325135i | 10.798674+0.0001i |  | 0.0108+23.275141i | 0.114298+251.340661i | 10.809474+23.275241i | 8.884624+4.121281i | 8.884724+2.921428i | 21.6 | 9.3527 | [6 empty] | 0 | 0
|  | Harm # |  |  | Amps | [10 empty] | Quantity: | 3 | [16 empty] | Iron-Core Reactor Losses, 60 Hertz: | [6 empty] | 2756.5238 |  |  | Watts, 3-Phase or 9406 BTUs/Hour | [11 empty] | 21.8 | 0.0001-1.188845i | 0.000001-0.049535i | 0.010799+23.541108i | 10.798674+0.0001i |  | 0.0108+23.491573i | 0.114277+253.67784i | 10.809474+23.491673i | 8.913596+4.096643i | 8.913696+2.907798i | 21.8 | 9.376 | [6 empty] | 0 | 0
|  | 1 |  |  | 417.1862 | [10 empty] | Number of Phases: | 1 | [16 empty] | Total 60 Hz Losses: | [6 empty] | 10285.7508 |  |  | Watts, 3-Phase or 35096 BTUs/Hour | [11 empty] | 22 | 0.0001-1.178037i | 0.000001-0.049085i | 0.010799+23.757082i | 10.798674+0.0001i |  | 0.0108+23.707997i | 0.114255+256.014932i | 10.809474+23.708097i | 8.941959+4.072179i | 8.942059+2.894142i | 22 | 9.3987 | [6 empty] | 4.1239 | 17.0068
|  | 2 |  |  | 0 | [10 empty] | System Voltage: | 12.47 |  | kV | [36 empty] | 22.2 | 0.0001-1.167424i | 0.000001-0.048643i | 0.010799+23.973055i | 10.798674+0.0001i |  | 0.0108+23.924412i | 0.114233+258.351927i | 10.809474+23.924512i | 8.969728+4.047891i | 8.969828+2.880467i | 22.2 | 9.421 | [6 empty] | 3.9163 | 15.3374
|  | 3 |  |  | 0 | [10 empty] | BIL Rating: | 95 |  | kV | [13 empty] | Harmonic Losses Based on Specified Harmonics | [22 empty] | 22.4 | 0.0001-1.157001i | 0.000001-0.048208i | 0.010799+24.189029i | 10.798674+0.0001i |  | 0.0108+24.140821i | 0.114212+260.688857i | 10.809474+24.140921i | 8.996919+4.02378i | 8.997019+2.866779i | 22.4 | 9.4427 | [7 empty] | 206963.4607
|  | 4 |  |  | 0 | [10 empty] | 60 Second Withstand Voltage: | 35 |  | kV | [14 empty] | High-Pass Resistor Losses: | [6 empty] | 232256.141 |  |  | Watts, 3-Phase or 792491 BTUs/Hour | [11 empty] | 22.6 | 0.0001-1.146762i | 0.000001-0.047782i | 0.010799+24.405002i | 10.798674+0.0001i |  | 0.0108+24.35722i | 0.11419+263.025679i | 10.809474+24.35732i | 9.023547+3.999849i | 9.023647+2.853087i | 22.6 | 9.4639 | [7 empty] | 454.9324 | reactor RMS amps (for supplier with margin)
|  | 5 |  |  | 135.2285 | [10 empty] | Fundamental Frequency: | 60 |  | Hz | [14 empty] | Iron-Core Reactor Losses: | [6 empty] | 473.9771 |  |  | Watts, 3-Phase or 1617 BTUs/Hour | [11 empty] | 22.8 | 0.0001-1.136702i | 0.000001-0.047363i | 0.010799+24.620976i | 10.798674+0.0001i |  | 0.0108+24.573613i | 0.114168+265.362437i | 10.809474+24.573713i | 9.049625+3.976099i | 9.049725+2.839397i | 22.8 | 9.4847
|  | 7 |  |  | 98.9675 | [10 empty] | Inductance: | 2.8645 |  | mH | [14 empty] | Total Harmonic Losses: | [6 empty] | 232730.1181 |  |  | Watts, 3-Phase or 794108 BTUs/Hour | [11 empty] | 23 | 0.0001-1.126818i | 0.000001-0.046951i | 0.010799+24.836949i | 10.798674+0.0001i |  | 0.0108+24.789998i | 0.114147+267.699108i | 10.809474+24.790098i | 9.075169+3.952532i | 9.075269+2.825714i | 23 | 9.505
|  | 11 |  |  | 60.8152 | [10 empty] | Reactance at 60Hz: | 1.0799 |  | Ohms | [36 empty] | 23.2 | 0.0001-1.117104i | 0.000001-0.046546i | 0.010799+25.052923i | 10.798674+0.0001i |  | 0.0108+25.006377i | 0.114125+270.035714i | 10.809474+25.006477i | 9.10019+3.929148i | 9.10029+2.812044i | 23.2 | 9.5249
|  | 13 |  |  | 27.5392 | [10 empty] | Taps: | None | [16 empty] | Total Losses - All: | [6 empty] | 243015.8689 |  |  | Watts, 3-Phase or 829204 BTUs/Hour | [11 empty] | 23.4 | 0.0001-1.107556i | 0.000001-0.046148i | 0.010799+25.268896i | 10.798674+0.0001i |  | 0.0108+25.222748i | 0.114103+272.372234i | 10.809474+25.222848i | 9.124703+3.905948i | 9.124803+2.798392i | 23.4 | 9.5443
|  | 17 |  |  | 15.2498 | [10 empty] | Insulation Type: | Nomex | [38 empty] | 23.6 | 0.0001-1.09817i | 0.000001-0.045757i | 0.010799+25.48487i | 10.798674+0.0001i |  | 0.0108+25.439113i | 0.114082+274.708689i | 10.809474+25.439213i | 9.148719+3.882933i | 9.148819+2.784763i | 23.6 | 9.5633
|  | 19 |  |  | 7.0014 | [10 empty] | Ambient: | 60C | [38 empty] | 23.8 | 0.0001-1.088942i | 0.000001-0.045373i | 0.010799+25.700843i | 10.798674+0.0001i |  | 0.0108+25.65547i | 0.11406+277.045058i | 10.809474+25.65557i | 9.172252+3.860104i | 9.172352+2.771162i | 23.8 | 9.5818
|  | 23 |  |  | 5.9904 | [10 empty] | Temperature Rise: | 115C Rise over Ambient | [15 empty] | 🧮 HARMONIC FILTER DESIGN METHODOLOGY | [22 empty] | 24 | 0.0001-1.079867i | 0.000001-0.044994i | 0.010799+25.916817i | 10.798674+0.0001i |  | 0.0108+25.871823i | 0.114038+279.381383i | 10.809474+25.871923i | 9.195314+3.83746i | 9.195414+2.757593i | 24 | 9.6
|  | 25 |  |  | 5.5786 | [10 empty] | Winding Type: | CU/AL - Based On Price | [38 empty] | 24.2 | 0.0001-1.070943i | 0.000001-0.044623i | 0.010799+26.13279i | 10.798674+0.0001i |  | 0.0108+26.088167i | 0.114017+281.717612i | 10.809474+26.088267i | 9.217916+3.815002i | 9.218016+2.744059i | 24.2 | 9.6178
|  | 29 |  |  | 0 | [10 empty] | Tack Winding to Core: | Yes | [38 empty] | 24.4 | 0.0001-1.062165i | 0.000001-0.044257i | 0.010799+26.348764i | 10.798674+0.0001i |  | 0.0108+26.304507i | 0.113995+284.053797i | 10.809474+26.304607i | 9.240069+3.792731i | 9.240169+2.730566i | 24.4 | 9.6352
|  | 31 |  |  | 0 | [10 empty] | Enclosure: | None/Open Construction | [38 empty] | 24.6 | 0.0001-1.053529i | 0.000001-0.043897i | 0.010799+26.564737i | 10.798674+0.0001i |  | 0.0108+26.52084i | 0.113974+286.389906i | 10.809474+26.52094i | 9.261784+3.770645i | 9.261884+2.717116i | 24.6 | 9.6522
|  | 35 |  |  | 4.1239 | [50 empty] | 24.8 | 0.0001-1.045033i | 0.000001-0.043543i | 0.010799+26.780711i | 10.798674+0.0001i |  | 0.0108+26.737168i | 0.113952+288.725962i | 10.809474+26.737268i | 9.283073+3.748744i | 9.283173+2.703711i | 24.8 | 9.6689
|  | 37 |  |  | 3.9163 | [50 empty] | 25 | 0.0001-1.036673i | 0.000001-0.043195i | 0.010799+26.996684i | 10.798674+0.0001i |  | 0.0108+26.953489i | 0.11393+291.061942i | 10.809474+26.953589i | 9.303945+3.72703i | 9.304045+2.690357i | 25 | 9.6852
|  | RMS: |  |  | 454.9324 | [50 empty] | 25.2 | 0.0001-1.028445i | 0.000001-0.042852i | 0.010799+27.212658i | 10.798674+0.0001i |  | 0.0108+27.169806i | 0.113909+293.397879i | 10.809474+27.169906i | 9.324411+3.705499i | 9.324511+2.677054i | 25.2 | 9.7012
| Main Capacitor Group Specification | [54 empty] | 25.4 | 0.0001-1.020347i | 0.000001-0.042514i | 0.010799+27.428631i | 10.798674+0.0001i |  | 0.0108+27.386117i | 0.113887+295.733751i | 10.809474+27.386217i | 9.344481+3.684154i | 9.344581+2.663807i | 25.4 | 9.7168
| A quantity of 15, 766 kvar, 95 kV BIL, 60 Hertz, all-film, low-loss, double-bushing capacitors designed, manufactured, and tested to applicable IEEE/ANSI and IEC standards, supplied by Cooper, GE, or Hitachi (no others), are required for the main capacitor group. The capacitors shall be connected unground-wye and shall have applicable over-voltage and blown-fuse protection. | [54 empty] | 25.6 | 0.0001-1.012376i | 0.000001-0.042182i | 0.010799+27.644604i | 10.798674+0.0001i |  | 0.0108+27.602422i | 0.113865+298.069558i | 10.809474+27.602522i | 9.364164+3.662992i | 9.364264+2.650616i | 25.6 | 9.7322
[56 empty] | 25.8 | 0.0001-1.004528i | 0.000001-0.041855i | 0.010799+27.860578i | 10.798674+0.0001i |  | 0.0108+27.818723i | 0.113844+300.405322i | 10.809474+27.818823i | 9.383469+3.642013i | 9.383569+2.637485i | 25.8 | 9.7472
[56 empty] | 26 | 0.0001-0.996801i | 0.000001-0.041533i | 0.010799+28.076551i | 10.798674+0.0001i |  | 0.0108+28.035018i | 0.113822+302.741021i | 10.809474+28.035118i | 9.402406+3.621217i | 9.402506+2.624416i | 26 | 9.7619
[56 empty] | 26.2 | 0.0001-0.989191i | 0.000001-0.041216i | 0.010799+28.292525i | 10.798674+0.0001i |  | 0.0108+28.251309i | 0.113801+305.076677i | 10.809474+28.251409i | 9.420984+3.600602i | 9.421084+2.611411i | 26.2 | 9.7763
| Auxiliary Capacitor Group Specification | [54 empty] | 26.4 | 0.0001-0.981698i | 0.000001-0.040904i | 0.010799+28.508498i | 10.798674+0.0001i |  | 0.0108+28.467594i | 0.113779+307.412268i | 10.809474+28.467694i | 9.43921+3.580168i | 9.43931+2.59847i | 26.4 | 9.7904
| A quantity of 18, 154 kvar, 95 kV BIL, 60 Hertz, all-film, low-loss, double-bushing capacitors designed, manufactured, and tested to applicable IEEE/ANSI and IEC standards, supplied by Cooper, GE, or Hitachi (no others), are required for the auxiliary capacitor group. The capacitors shall be connected in series with the reactor. | [54 empty] | 26.6 | 0.0001-0.974316i | 0.000001-0.040597i | 0.010799+28.724472i | 10.798674+0.0001i |  | 0.0108+28.683875i | 0.113757+309.747816i | 10.809474+28.683975i | 9.457093+3.559913i | 9.457193+2.585597i | 26.6 | 9.8043
[56 empty] | 26.8 | 0.0001-0.967045i | 0.000001-0.040294i | 0.010799+28.940445i | 10.798674+0.0001i |  | 0.0108+28.900151i | 0.113736+312.08331i | 10.809474+28.900251i | 9.474642+3.539836i | 9.474742+2.572791i | 26.8 | 9.8178
[56 empty] | 27 | 0.0001-0.959882i | 0.000001-0.039995i | 0.010799+29.156419i | 10.798674+0.0001i |  | 0.0108+29.116424i | 0.113714+314.418772i | 10.809474+29.116524i | 9.491864+3.519938i | 9.491964+2.560056i | 27 | 9.8311
[56 empty] | 27.2 | 0.0001-0.952824i | 0.000001-0.039701i | 0.010799+29.372392i | 10.798674+0.0001i |  | 0.0108+29.332691i | 0.113692+316.754169i | 10.809474+29.332791i | 9.508767+3.500215i | 9.508867+2.547391i | 27.2 | 9.8442
| High-Pass Resistor specification | [54 empty] | 27.4 | 0.0001-0.945869i | 0.000001-0.039411i | 0.010799+29.588366i | 10.798674+0.0001i |  | 0.0108+29.548955i | 0.113671+319.089533i | 10.809474+29.549055i | 9.525359+3.480668i | 9.525459+2.534799i | 27.4 | 9.857
| A quantity of 3 stainless steel grid resistors shall be provided. Each resistor shall have an ohmic value per phase of 10.8 ohms, a continuous power rating of 77.42 kW, and an RMS current rating of 84.67 amps. The resistor element shall be divided into 2 series groups to ensure adequate withstand voltage during switching transients, with the overall BIL rating coordinated to 95 kV. | [54 empty] | 27.6 | 0.0001-0.939015i | 0.000001-0.039126i | 0.010799+29.804339i | 10.798674+0.0001i |  | 0.0108+29.765213i | 0.113649+321.424833i | 10.809474+29.765313i | 9.541645+3.461295i | 9.541745+2.52228i | 27.6 | 9.8695
[56 empty] | 27.8 | 0.0001-0.93226i | 0.000001-0.038844i | 0.010799+30.020313i | 10.798674+0.0001i |  | 0.0108+29.981469i | 0.113628+323.760111i | 10.809474+29.981569i | 9.557635+3.442094i | 9.557735+2.509834i | 27.8 | 9.8818
[56 empty] | 28 | 0.0001-0.925601i | 0.000001-0.038567i | 0.010799+30.236286i | 10.798674+0.0001i |  | 0.0108+30.197719i | 0.113606+326.095324i | 10.809474+30.197819i | 9.573334+3.423065i | 9.573434+2.497464i | 28 | 9.8938
[56 empty] | 28.2 | 0.0001-0.919036i | 0.000001-0.038293i | 0.010799+30.45226i | 10.798674+0.0001i |  | 0.0108+30.413967i | 0.113584+328.430516i | 10.809474+30.414067i | 9.588749+3.404206i | 9.588849+2.48517i | 28.2 | 9.9057
|  | Info@VarStec.com | [29 empty] | 5 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 6 ¦ P a g e |  |  |  |  | 28.4 | 0.0001-0.912564i | 0.000001-0.038023i | 0.010799+30.668233i | 10.798674+0.0001i |  | 0.0108+30.63021i | 0.113563+330.765653i | 10.809474+30.63031i | 9.603886+3.385516i | 9.603986+2.472952i | 28.4 | 9.9173
[56 empty] | 28.6 | 0.0001-0.906182i | 0.000001-0.037758i | 0.010799+30.884207i | 10.798674+0.0001i |  | 0.0108+30.846449i | 0.113541+333.100748i | 10.809474+30.846549i | 9.618753+3.366993i | 9.618853+2.460811i | 28.6 | 9.9286
[56 empty] | 28.8 | 0.0001-0.899889i | 0.000001-0.037495i | 0.010799+31.10018i | 10.798674+0.0001i |  | 0.0108+31.062685i | 0.113519+335.43581i | 10.809474+31.062785i | 9.633354+3.348636i | 9.633454+2.448747i | 28.8 | 9.9398
[56 empty] | 29 | 0.0001-0.893683i | 0.000001-0.037237i | 0.010799+31.316153i | 10.798674+0.0001i |  | 0.0108+31.278916i | 0.113498+337.770818i | 10.809474+31.279016i | 9.647697+3.330445i | 9.647797+2.436762i | 29 | 9.9508
[56 empty] | 29.2 | 0.0001-0.887562i | 0.000001-0.036982i | 0.010799+31.532127i | 10.798674+0.0001i |  | 0.0108+31.495145i | 0.113476+340.105805i | 10.809474+31.495245i | 9.661786+3.312416i | 9.661886+2.424854i | 29.2 | 9.9615
[56 empty] | 29.4 | 0.0001-0.881524i | 0.000001-0.03673i | 0.010799+31.7481i | 10.798674+0.0001i |  | 0.0108+31.71137i | 0.113455+342.440748i | 10.809474+31.71147i | 9.675629+3.294549i | 9.675729+2.413025i | 29.4 | 9.9721
| Enter Customer PO # ¦ Stage 1 | [31 empty] | Enter Customer PO # ¦ Stage 1 | [22 empty] | 29.6 | 0.0001-0.875568i | 0.000001-0.036482i | 0.010799+31.964074i | 10.798674+0.0001i |  | 0.0108+31.927592i | 0.113433+344.775659i | 10.809474+31.927692i | 9.689229+3.276843i | 9.689329+2.401275i | 29.6 | 9.9824
[56 empty] | 29.8 | 0.0001-0.869692i | 0.000001-0.036237i | 0.010799+32.180047i | 10.798674+0.0001i |  | 0.0108+32.14381i | 0.113411+347.110526i | 10.809474+32.14391i | 9.702592+3.259296i | 9.702692+2.389604i | 29.8 | 9.9926
[33 empty] | Nomenclature and Parameter Definitions for Harmonic Filter Design | [22 empty] | 30 | 0.0001-0.863894i | 0.000001-0.035996i | 0.010799+32.396021i | 10.798674+0.0001i |  | 0.0108+32.360025i | 0.11339+349.445362i | 10.809474+32.360125i | 9.715725+3.241906i | 9.715825+2.378012i | 30 | 10.0026
[35 empty] | Xeff: |  | Effective reactance of the harmonic filter | [18 empty] | 30.2 | 0.0001-0.858173i | 0.000001-0.035757i | 0.010799+32.611994i | 10.798674+0.0001i |  | 0.0108+32.576237i | 0.113368+351.780165i | 10.809474+32.576337i | 9.728631+3.224672i | 9.728731+2.366499i | 30.2 | 10.0124
[35 empty] | Qeff: |  | Effective reactive power output of the harmonic filter (considering fundamental current only) | [18 empty] | 30.4 | 0.0001-0.852527i | 0.000001-0.035522i | 0.010799+32.827968i | 10.798674+0.0001i |  | 0.0108+32.792446i | 0.113346+354.114935i | 10.809474+32.792546i | 9.741316+3.207593i | 9.741416+2.355066i | 30.4 | 10.0221
[35 empty] | QMAIN RATED PER PHASE: |  | kvar rating of main capacitor group at their rated voltage (not the application voltage) | [18 empty] | 30.6 | 0.0001-0.846955i | 0.000001-0.03529i | 0.010799+33.043941i | 10.798674+0.0001i |  | 0.0108+33.008651i | 0.113325+356.449662i | 10.809474+33.008751i | 9.753784+3.190667i | 9.753884+2.343712i | 30.6 | 10.0315
[35 empty] | VLLSYS: |  | Nominal system line-to-line voltage | [18 empty] | 30.8 | 0.0001-0.841455i | 0.000001-0.035061i | 0.010799+33.259915i | 10.798674+0.0001i |  | 0.0108+33.224854i | 0.113303+358.784368i | 10.809474+33.224954i | 9.766041+3.173893i | 9.766141+2.332438i | 30.8 | 10.0408
[35 empty] | XC: |  | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [18 empty] | 31 | 0.0001-0.836026i | 0.000001-0.034834i | 0.010799+33.475888i | 10.798674+0.0001i |  | 0.0108+33.441054i | 0.113282+361.119041i | 10.809474+33.441154i | 9.77809+3.157269i | 9.77819+2.321243i | 31 | 10.0499
[35 empty] | XL: |  | Inductive reactance of the harmonic filter reactor at fundamental frequency | [18 empty] | 31.2 | 0.0001-0.830667i | 0.000001-0.034611i | 0.010799+33.691862i | 10.798674+0.0001i |  | 0.0108+33.657251i | 0.11326+363.453682i | 10.809474+33.657351i | 9.789937+3.140794i | 9.790037+2.310127i | 31.2 | 10.0589
[35 empty] | hn: |  | harmonic number of filter tuning point | [18 empty] | 31.4 | 0.0001-0.825376i | 0.000001-0.034391i | 0.010799+33.907835i | 10.798674+0.0001i |  | 0.0108+33.873444i | 0.113238+365.78828i | 10.809474+33.873544i | 9.801586+3.124466i | 9.801686+2.29909i | 31.4 | 10.0677
[35 empty] | hf: |  | harmonic frequency of filter tuning point in Hertz | [18 empty] | 31.6 | 0.0001-0.820152i | 0.000001-0.034173i | 0.010799+34.123809i | 10.798674+0.0001i |  | 0.0108+34.089636i | 0.113217+368.122867i | 10.809474+34.089736i | 9.81304+3.108284i | 9.81314+2.288132i | 31.6 | 10.0764
[35 empty] | f: |  | frequency | [18 empty] | 31.8 | 0.0001-0.814994i | 0.000001-0.033958i | 0.010799+34.339782i | 10.798674+0.0001i |  | 0.0108+34.305824i | 0.113195+370.457411i | 10.809474+34.305924i | 9.824305+3.092246i | 9.824405+2.277252i | 31.8 | 10.0849
[35 empty] | HL: |  | Reactor Henry rating (millihenries) | [18 empty] | 32 | 0.0001-0.809901i | 0.000001-0.033746i | 0.010799+34.555756i | 10.798674+0.0001i |  | 0.0108+34.52201i | 0.113173+372.791933i | 10.809474+34.52211i | 9.835383+3.076352i | 9.835483+2.266451i | 32 | 10.0932
[35 empty] | IRATED FUNDAMENTAL : |  | Fundamental current rating of filter bank | [18 empty] | 32.2 | 0.0001-0.80487i | 0.000001-0.033536i | 0.010799+34.771729i | 10.798674+0.0001i |  | 0.0108+34.738193i | 0.113152+375.126423i | 10.809474+34.738293i | 9.84628+3.060598i | 9.84638+2.255728i | 32.2 | 10.1015
[34 empty] | VCAP FUNDAMENTAL VOLTAGE: |  |  | Fundamental voltage drop across capacitor | [18 empty] | 32.4 | 0.0001-0.799902i | 0.000001-0.033329i | 0.010799+34.987703i | 10.798674+0.0001i |  | 0.0108+34.954374i | 0.11313+377.460891i | 10.809474+34.954474i | 9.856999+3.044985i | 9.857099+2.245083i | 32.4 | 10.1095
[35 empty] | VCAP HARMONIC VOLTAGE: |  | Harmonic voltage drop across capacitor | [18 empty] | 32.6 | 0.0001-0.794994i | 0.000001-0.033125i | 0.010799+35.203676i | 10.798674+0.0001i |  | 0.0108+35.170551i | 0.113109+379.795316i | 10.809474+35.170651i | 9.867543+3.02951i | 9.867643+2.234516i | 32.6 | 10.1175
| 🧮 FORMULAS | [33 empty] | VCAP MAIN RMS VOLTAGE: |  | Main capacitor RMS voltage (fundamental voltage + harmonic voltages) | [18 empty] | 32.8 | 0.0001-0.790147i | 0.000001-0.032923i | 0.010799+35.419649i | 10.798674+0.0001i |  | 0.0108+35.386726i | 0.113087+382.129719i | 10.809474+35.386826i | 9.877916+3.014172i | 9.878016+2.224025i | 32.8 | 10.1253
[35 empty] | VPEAK CAP VOLTAGE: |  | Capacitor voltage assuming or harmonics are coincident | [18 empty] | 33 | 0.0001-0.785358i | 0.000001-0.032723i | 0.010799+35.635623i | 10.798674+0.0001i |  | 0.0108+35.6029i | 0.113065+384.464112i | 10.809474+35.603i | 9.888122+2.99897i | 9.888222+2.213612i | 33 | 10.133
| The below shows how a 1000 kvar 13.8kV 4.7th tuned C-HP Filter Design is computed manually and is the basis this spreadsheet. | [34 empty] | VCAP MAIN RMS VOLTAGE: | Capacitor (main group) RMS voltage including harmonics | [18 empty] | 33.2 | 0.0001-0.780627i | 0.000001-0.032526i | 0.010799+35.851596i | 10.798674+0.0001i |  | 0.0108+35.81907i | 0.113044+386.798461i | 10.809474+35.81917i | 9.898165+2.983902i | 9.898265+2.203275i | 33.2 | 10.1405
[36 empty] | VCAP MAIN, PEAK CAP VOLTAGE: | Capacitor (main group) peak voltage, including harmonics, and assuming peaks are in phase. | [18 empty] | 33.4 | 0.0001-0.775953i | 0.000001-0.032331i | 0.010799+36.06757i | 10.798674+0.0001i |  | 0.0108+36.035239i | 0.113022+389.1328i | 10.809474+36.035339i | 9.908047+2.968968i | 9.908147+2.193015i | 33.4 | 10.1479
[35 empty] | N: |  | Number of capacitors per phase | [18 empty] | 33.6 | 0.0001-0.771334i | 0.000001-0.032139i | 0.010799+36.283543i | 10.798674+0.0001i |  | 0.0108+36.251404i | 0.113001+391.467095i | 10.809474+36.251504i | 9.917772+2.954164i | 9.917872+2.18283i | 33.6 | 10.1552
[35 empty] | VCAP VAR RATING: |  | Capacitor can var rating (in Kvar) | [18 empty] | 33.8 | 0.0001-0.76677i | 0.000001-0.031949i | 0.010799+36.499517i | 10.798674+0.0001i |  | 0.0108+36.467568i | 0.112979+393.801379i | 10.809474+36.467668i | 9.927343+2.939491i | 9.927443+2.172721i | 33.8 | 10.1624
[35 empty] | ICAP RMS CURRENT: |  | RMS current seen by capacitor (amps rms) | [18 empty] | 34 | 0.0001-0.762259i | 0.000001-0.031761i | 0.010799+36.71549i | 10.798674+0.0001i |  | 0.0108+36.683729i | 0.112957+396.135632i | 10.809474+36.683829i | 9.936763+2.924946i | 9.936863+2.162687i | 34 | 10.1695
[35 empty] | IFILTER RMS CURRENT: |  | RMS current into filter branch (amps rms) | [18 empty] | 34.2 | 0.0001-0.757802i | 0.000001-0.031575i | 0.010799+36.931464i | 10.798674+0.0001i |  | 0.0108+36.899889i | 0.112936+398.469873i | 10.809474+36.899989i | 9.946035+2.910529i | 9.946135+2.152727i | 34.2 | 10.1764
[35 empty] | DF: |  | Damping Factor is R/XLn at the tuning harmonic number (hn), where XLn=XL x hn | [18 empty] | 34.4 | 0.0001-0.753396i | 0.000001-0.031391i | 0.010799+37.147437i | 10.798674+0.0001i |  | 0.0108+37.116046i | 0.112914+400.804082i | 10.809474+37.116146i | 9.955163+2.896237i | 9.955263+2.142841i | 34.4 | 10.1833
[36 empty] | XCA | Capacitive reactance of auxiliary capacitor group (ohms/phase) | [18 empty] | 34.6 | 0.0001-0.749041i | 0.000001-0.03121i | 0.010799+37.363411i | 10.798674+0.0001i |  | 0.0108+37.332201i | 0.112892+403.138269i | 10.809474+37.332301i | 9.964149+2.88207i | 9.964249+2.133029i | 34.6 | 10.19
[36 empty] | XCM | Capacitive reactance of main capacitor group (ohm/phase) | [18 empty] | 34.8 | 0.0001-0.744736i | 0.000001-0.031031i | 0.010799+37.579384i | 10.798674+0.0001i |  | 0.0108+37.548353i | 0.112871+405.472424i | 10.809474+37.548453i | 9.972996+2.868027i | 9.973096+2.123291i | 34.8 | 10.1966
[36 empty] | R | Resistance of high-pass damping resistor | [18 empty] | 35 | 0.0001-0.74048i | 0.000001-0.030853i | 0.010799+37.795358i | 10.798674+0.0001i |  | 0.0108+37.764505i | 0.112849+407.806579i | 10.809474+37.764605i | 9.981707+2.854105i | 9.981807+2.113625i | 35 | 10.2031
[36 empty] | In | Current in amps at each harmonic | [18 empty] | 35.2 | 0.0001-0.736273i | 0.000001-0.030678i | 0.010799+38.011331i | 10.798674+0.0001i |  | 0.0108+37.980653i | 0.112828+410.140691i | 10.809474+37.980753i | 9.990284+2.840304i | 9.990384+2.104031i | 35.2 | 10.2095
[56 empty] | 35.4 | 0.0001-0.732113i | 0.000001-0.030505i | 0.010799+38.227305i | 10.798674+0.0001i |  | 0.0108+38.1968i | 0.112806+412.474792i | 10.809474+38.1969i | 9.99873+2.826622i | 9.99883+2.094509i | 35.4 | 10.2158
[33 empty] | Disclaimer and Use Limitation | [22 empty] | 35.6 | 0.0001-0.728i | 0.000001-0.030333i | 0.010799+38.443278i | 10.798674+0.0001i |  | 0.0108+38.412945i | 0.112784+414.808872i | 10.809474+38.413045i | 10.007048+2.813058i | 10.007148+2.085058i | 35.6 | 10.2221
[33 empty] | This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool. | [22 empty] | 35.8 | 0.0001-0.723933i | 0.000001-0.030164i | 0.010799+38.659252i | 10.798674+0.0001i |  | 0.0108+38.629088i | 0.112763+417.142929i | 10.809474+38.629188i | 10.01524+2.799611i | 10.01534+2.075678i | 35.8 | 10.2282
[56 empty] | 36 | 0.0001-0.719912i | 0.000001-0.029996i | 0.010799+38.875225i | 10.798674+0.0001i |  | 0.0108+38.845229i | 0.112741+419.476966i | 10.809474+38.845329i | 10.023309+2.78628i | 10.023409+2.066368i | 36 | 10.2342
[56 empty] | 36.2 | 0.0001-0.715934i | 0.000001-0.029831i | 0.010799+39.091198i | 10.798674+0.0001i |  | 0.0108+39.061367i | 0.11272+421.810969i | 10.809474+39.061467i | 10.031257+2.773063i | 10.031357+2.057129i | 36.2 | 10.2401
| One-Line Diagram C-High-Pass Filter Design Parameters | [54 empty] | 36.4 | 0.0001-0.712i | 0.000001-0.029667i | 0.010799+39.307172i | 10.798674+0.0001i |  | 0.0108+39.277505i | 0.112698+424.144973i | 10.809474+39.277605i | 10.039087+2.759958i | 10.039187+2.047958i | 36.4 | 10.2459
[56 empty] | 36.6 | 0.0001-0.70811i | 0.000001-0.029505i | 0.010799+39.523145i | 10.798674+0.0001i |  | 0.0108+39.49364i | 0.112676+426.478945i | 10.809474+39.49374i | 10.0468+2.746966i | 10.0469+2.038856i | 36.6 | 10.2517
[56 empty] | 36.8 | 0.0001-0.704261i | 0.000001-0.029344i | 0.010799+39.739119i | 10.798674+0.0001i |  | 0.0108+39.709775i | 0.112655+428.812916i | 10.809474+39.709875i | 10.054399+2.734083i | 10.054499+2.029822i | 36.8 | 10.2573
[56 empty] | 37 | 0.0001-0.700455i | 0.000001-0.029186i | 0.010799+39.955092i | 10.798674+0.0001i |  | 0.0108+39.925906i | 0.112633+431.146844i | 10.809474+39.926006i | 10.061886+2.72131i | 10.061986+2.020855i | 37 | 10.2629
[56 empty] | 37.2 | 0.0001-0.696689i | 0.000001-0.029029i | 0.010799+40.171066i | 10.798674+0.0001i |  | 0.0108+40.142037i | 0.112611+433.480772i | 10.809474+40.142137i | 10.069263+2.708646i | 10.069363+2.011957i | 37.2 | 10.2684
[56 empty] | 37.4 | 0.0001-0.692963i | 0.000001-0.028873i | 0.010799+40.387039i | 10.798674+0.0001i |  | 0.0108+40.358166i | 0.11259+435.814679i | 10.809474+40.358266i | 10.076533+2.696088i | 10.076633+2.003125i | 37.4 | 10.2738
[56 empty] | 37.6 | 0.0001-0.689277i | 0.000001-0.02872i | 0.010799+40.603013i | 10.798674+0.0001i |  | 0.0108+40.574293i | 0.112568+438.148564i | 10.809474+40.574393i | 10.083697+2.683636i | 10.083797+1.994359i | 37.6 | 10.2791
[56 empty] | 37.8 | 0.0001-0.68563i | 0.000001-0.028568i | 0.010799+40.818986i | 10.798674+0.0001i |  | 0.0108+40.790418i | 0.112547+440.482427i | 10.809474+40.790518i | 10.090757+2.671288i | 10.090857+1.985658i | 37.8 | 10.2844
[56 empty] | 38 | 0.0001-0.682021i | 0.000001-0.028418i | 0.010799+41.03496i | 10.798674+0.0001i |  | 0.0108+41.006542i | 0.112525+442.81628i | 10.809474+41.006642i | 10.097716+2.659044i | 10.097816+1.977023i | 38 | 10.2895
|  | Info@VarStec.com | [29 empty] | 7 ¦ P a g e |  | Info@VarStec.com | [16 empty] | 8 ¦ P a g e |  |  |  |  | 38.2 | 0.0001-0.678451i | 0.000001-0.028269i | 0.010799+41.250933i | 10.798674+0.0001i |  | 0.0108+41.222664i | 0.112503+445.150111i | 10.809474+41.222764i | 10.104574+2.646902i | 10.104674+1.968451i | 38.2 | 10.2946
[56 empty] | 38.4 | 0.0001-0.674917i | 0.000001-0.028122i | 0.010799+41.466907i | 10.798674+0.0001i |  | 0.0108+41.438785i | 0.112482+447.483931i | 10.809474+41.438885i | 10.111335+2.634862i | 10.111435+1.959945i | 38.4 | 10.2996
[56 empty] | 38.6 | 0.0001-0.67142i | 0.000001-0.027976i | 0.010799+41.68288i | 10.798674+0.0001i |  | 0.0108+41.654904i | 0.11246+449.81773i | 10.809474+41.655004i | 10.118+2.622921i | 10.1181+1.951501i | 38.6 | 10.3046
[56 empty] | 38.8 | 0.0001-0.667959i | 0.000001-0.027832i | 0.010799+41.898854i | 10.798674+0.0001i |  | 0.0108+41.871022i | 0.112439+452.151518i | 10.809474+41.871122i | 10.12457+2.61108i | 10.12467+1.943121i | 38.8 | 10.3094
[56 empty] | 39 | 0.0001-0.664534i | 0.000001-0.027689i | 0.010799+42.114827i | 10.798674+0.0001i |  | 0.0108+42.087138i | 0.112417+454.485284i | 10.809474+42.087238i | 10.131048+2.599336i | 10.131148+1.934802i | 39 | 10.3142
[56 empty] | 39.2 | 0.0001-0.661143i | 0.000001-0.027548i | 0.010799+42.330801i | 10.798674+0.0001i |  | 0.0108+42.303253i | 0.112395+456.819039i | 10.809474+42.303353i | 10.137435+2.587689i | 10.137535+1.926546i | 39.2 | 10.319
[56 empty] | 39.4 | 0.0001-0.657787i | 0.000001-0.027408i | 0.010799+42.546774i | 10.798674+0.0001i |  | 0.0108+42.519366i | 0.112374+459.152773i | 10.809474+42.519466i | 10.143732+2.576139i | 10.143832+1.918352i | 39.4 | 10.3236
[56 empty] | 39.6 | 0.0001-0.654465i | 0.000001-0.027269i | 0.010799+42.762748i | 10.798674+0.0001i |  | 0.0108+42.735479i | 0.112352+461.486507i | 10.809474+42.735579i | 10.149942+2.564682i | 10.150042+1.910217i | 39.6 | 10.3282
[56 empty] | 39.8 | 0.0001-0.651176i | 0.000001-0.027132i | 0.010799+42.978721i | 10.798674+0.0001i |  | 0.0108+42.951589i | 0.112331+463.820208i | 10.809474+42.951689i | 10.156065+2.55332i | 10.156165+1.902144i | 39.8 | 10.3328
[56 empty] | 40 | 0.0001-0.64792i | 0.000001-0.026997i | 0.010799+43.194694i | 10.798674+0.0001i |  | 0.0108+43.167697i | 0.112309+466.153888i | 10.809474+43.167797i | 10.162105+2.54205i | 10.162205+1.89413i | 40 | 10.3372
[56 empty] | 40.2 | 0.0001-0.644697i | 0.000001-0.026862i | 0.010799+43.410668i | 10.798674+0.0001i |  | 0.0108+43.383806i | 0.112287+468.487579i | 10.809474+43.383906i | 10.168061+2.530872i | 10.168161+1.886175i | 40.2 | 10.3416
[56 empty] | 40.4 | 0.0001-0.641505i | 0.000001-0.026729i | 0.010799+43.626641i | 10.798674+0.0001i |  | 0.0108+43.599912i | 0.112266+470.821237i | 10.809474+43.600012i | 10.173935+2.519784i | 10.174035+1.878279i | 40.4 | 10.346
[56 empty] | 40.6 | 0.0001-0.638345i | 0.000001-0.026598i | 0.010799+43.842615i | 10.798674+0.0001i |  | 0.0108+43.816017i | 0.112244+473.154885i | 10.809474+43.816117i | 10.17973+2.508786i | 10.17983+1.870441i | 40.6 | 10.3502
[56 empty] | 40.8 | 0.0001-0.635216i | 0.000001-0.026467i | 0.010799+44.058588i | 10.798674+0.0001i |  | 0.0108+44.032121i | 0.112222+475.488521i | 10.809474+44.032221i | 10.185445+2.497877i | 10.185545+1.862661i | 40.8 | 10.3545
[56 empty] | 41 | 0.0001-0.632117i | 0.000001-0.026338i | 0.010799+44.274562i | 10.798674+0.0001i |  | 0.0108+44.248224i | 0.112201+477.822147i | 10.809474+44.248324i | 10.191084+2.487056i | 10.191184+1.854939i | 41 | 10.3586
[56 empty] | 41.2 | 0.0001-0.629049i | 0.000001-0.02621i | 0.010799+44.490535i | 10.798674+0.0001i |  | 0.0108+44.464325i | 0.112179+480.155751i | 10.809474+44.464425i | 10.196646+2.476321i | 10.196746+1.847272i | 41.2 | 10.3627
[56 empty] | 41.4 | 0.0001-0.62601i | 0.000001-0.026084i | 0.010799+44.706509i | 10.798674+0.0001i |  | 0.0108+44.680425i | 0.112158+482.489345i | 10.809474+44.680525i | 10.202134+2.465673i | 10.202234+1.839663i | 41.4 | 10.3668
[56 empty] | 41.6 | 0.0001-0.623i | 0.000001-0.025958i | 0.010799+44.922482i | 10.798674+0.0001i |  | 0.0108+44.896524i | 0.112136+484.822927i | 10.809474+44.896624i | 10.207549+2.455109i | 10.207649+1.832109i | 41.6 | 10.3708
[56 empty] | 41.8 | 0.0001-0.62002i | 0.000001-0.025834i | 0.010799+45.138456i | 10.798674+0.0001i |  | 0.0108+45.112622i | 0.112114+487.156499i | 10.809474+45.112722i | 10.212892+2.444629i | 10.212992+1.824609i | 41.8 | 10.3747
[56 empty] | 42 | 0.0001-0.617067i | 0.000001-0.025711i | 0.010799+45.354429i | 10.798674+0.0001i |  | 0.0108+45.328718i | 0.112093+489.49005i | 10.809474+45.328818i | 10.218164+2.434232i | 10.218264+1.817165i | 42 | 10.3786
[56 empty] | 42.2 | 0.0001-0.614143i | 0.000001-0.025589i | 0.010799+45.570403i | 10.798674+0.0001i |  | 0.0108+45.544814i | 0.112071+491.8236i | 10.809474+45.544914i | 10.223366+2.423918i | 10.223466+1.809775i | 42.2 | 10.3824
[56 empty] | 42.4 | 0.0001-0.611246i | 0.000001-0.025469i | 0.010799+45.786376i | 10.798674+0.0001i |  | 0.0108+45.760907i | 0.11205+494.157118i | 10.809474+45.761007i | 10.2285+2.413685i | 10.2286+1.802439i | 42.4 | 10.3862
[56 empty] | 42.6 | 0.0001-0.608376i | 0.000001-0.025349i | 0.010799+46.00235i | 10.798674+0.0001i |  | 0.0108+45.977001i | 0.112028+496.490646i | 10.809474+45.977101i | 10.233567+2.403532i | 10.233667+1.795156i | 42.6 | 10.3899
[56 empty] | 42.8 | 0.0001-0.605533i | 0.000001-0.025231i | 0.010799+46.218323i | 10.798674+0.0001i |  | 0.0108+46.193092i | 0.112006+498.824143i | 10.809474+46.193192i | 10.238567+2.393459i | 10.238667+1.787926i | 42.8 | 10.3936
[56 empty] | 43 | 0.0001-0.602717i | 0.000001-0.025113i | 0.010799+46.434297i | 10.798674+0.0001i |  | 0.0108+46.409184i | 0.111985+501.15765i | 10.809474+46.409284i | 10.243503+2.383465i | 10.243603+1.780748i | 43 | 10.3972
[56 empty] | 43.2 | 0.0001-0.599926i | 0.000001-0.024997i | 0.010799+46.65027i | 10.798674+0.0001i |  | 0.0108+46.625273i | 0.111963+503.491124i | 10.809474+46.625373i | 10.248375+2.373548i | 10.248475+1.773622i | 43.2 | 10.4008
[56 empty] | 43.4 | 0.0001-0.597162i | 0.000001-0.024882i | 0.010799+46.866243i | 10.798674+0.0001i |  | 0.0108+46.841361i | 0.111942+505.824588i | 10.809474+46.841461i | 10.253184+2.363709i | 10.253284+1.766547i | 43.4 | 10.4044
[56 empty] | 43.6 | 0.0001-0.594422i | 0.000001-0.024768i | 0.010799+47.082217i | 10.798674+0.0001i |  | 0.0108+47.057449i | 0.11192+508.158052i | 10.809474+47.057549i | 10.257932+2.353946i | 10.258032+1.759524i | 43.6 | 10.4078
[56 empty] | 43.8 | 0.0001-0.591708i | 0.000001-0.024655i | 0.010799+47.29819i | 10.798674+0.0001i |  | 0.0108+47.273535i | 0.111898+510.491494i | 10.809474+47.273635i | 10.262619+2.344258i | 10.262719+1.75255i | 43.8 | 10.4113
[56 empty] | 44 | 0.0001-0.589019i | 0.000001-0.024542i | 0.010799+47.514164i | 10.798674+0.0001i |  | 0.0108+47.489622i | 0.111877+512.824947i | 10.809474+47.489722i | 10.267246+2.334645i | 10.267346+1.745626i | 44 | 10.4147
[56 empty] | 44.2 | 0.0001-0.586353i | 0.000001-0.024431i | 0.010799+47.730137i | 10.798674+0.0001i |  | 0.0108+47.705706i | 0.111855+515.158368i | 10.809474+47.705806i | 10.271815+2.325106i | 10.271915+1.738753i | 44.2 | 10.418
[56 empty] | 44.4 | 0.0001-0.583712i | 0.000001-0.024321i | 0.010799+47.946111i | 10.798674+0.0001i |  | 0.0108+47.92179i | 0.111834+517.491789i | 10.809474+47.92189i | 10.276325+2.31564i | 10.276425+1.731928i | 44.4 | 10.4213
[56 empty] | 44.6 | 0.0001-0.581095i | 0.000001-0.024212i | 0.010799+48.162084i | 10.798674+0.0001i |  | 0.0108+48.137872i | 0.111812+519.825188i | 10.809474+48.137972i | 10.28078+2.306246i | 10.28088+1.725151i | 44.6 | 10.4246
[56 empty] | 44.8 | 0.0001-0.5785i | 0.000001-0.024104i | 0.010799+48.378058i | 10.798674+0.0001i |  | 0.0108+48.353954i | 0.11179+522.158587i | 10.809474+48.354054i | 10.285178+2.296924i | 10.285278+1.718424i | 44.8 | 10.4278
[56 empty] | 45 | 0.0001-0.575929i | 0.000001-0.023997i | 0.010799+48.594031i | 10.798674+0.0001i |  | 0.0108+48.570034i | 0.111769+524.491964i | 10.809474+48.570134i | 10.289521+2.287672i | 10.289621+1.711743i | 45 | 10.431
[56 empty] | 45.2 | 0.0001-0.573381i | 0.000001-0.023891i | 0.010799+48.810005i | 10.798674+0.0001i |  | 0.0108+48.786114i | 0.111747+526.825342i | 10.809474+48.786214i | 10.293811+2.278491i | 10.293911+1.70511i | 45.2 | 10.4342
[56 empty] | 45.4 | 0.0001-0.570855i | 0.000001-0.023786i | 0.010799+49.025978i | 10.798674+0.0001i |  | 0.0108+49.002192i | 0.111725+529.158698i | 10.809474+49.002292i | 10.298047+2.269378i | 10.298147+1.698523i | 45.4 | 10.4373
[56 empty] | 45.6 | 0.0001-0.568351i | 0.000001-0.023681i | 0.010799+49.241952i | 10.798674+0.0001i |  | 0.0108+49.218271i | 0.111704+531.492064i | 10.809474+49.218371i | 10.302231+2.260335i | 10.302331+1.691984i | 45.6 | 10.4403
[56 empty] | 45.8 | 0.0001-0.565869i | 0.000001-0.023578i | 0.010799+49.457925i | 10.798674+0.0001i |  | 0.0108+49.434347i | 0.111682+533.825399i | 10.809474+49.434447i | 10.306364+2.251359i | 10.306464+1.68549i | 45.8 | 10.4434
[56 empty] | 46 | 0.0001-0.563409i | 0.000001-0.023475i | 0.010799+49.673899i | 10.798674+0.0001i |  | 0.0108+49.650424i | 0.111661+536.158744i | 10.809474+49.650524i | 10.310446+2.24245i | 10.310546+1.679041i | 46 | 10.4464
[56 empty] | 46.2 | 0.0001-0.56097i | 0.000001-0.023374i | 0.010799+49.889872i | 10.798674+0.0001i |  | 0.0108+49.866498i | 0.111639+538.492057i | 10.809474+49.866598i | 10.314478+2.233608i | 10.314578+1.672638i | 46.2 | 10.4493
[56 empty] | 46.4 | 0.0001-0.558552i | 0.000001-0.023273i | 0.010799+50.105846i | 10.798674+0.0001i |  | 0.0108+50.082573i | 0.111617+540.82538i | 10.809474+50.082673i | 10.318461+2.224832i | 10.318561+1.66628i | 46.4 | 10.4522
[56 empty] | 46.6 | 0.0001-0.556155i | 0.000001-0.023173i | 0.010799+50.321819i | 10.798674+0.0001i |  | 0.0108+50.298646i | 0.111596+543.158682i | 10.809474+50.298746i | 10.322396+2.21612i | 10.322496+1.659965i | 46.6 | 10.4551
[56 empty] | 46.8 | 0.0001-0.553778i | 0.000001-0.023074i | 0.010799+50.537793i | 10.798674+0.0001i |  | 0.0108+50.514719i | 0.111574+545.491984i | 10.809474+50.514819i | 10.326284+2.207473i | 10.326384+1.653695i | 46.8 | 10.458
[56 empty] | 47 | 0.0001-0.551422i | 0.000001-0.022976i | 0.010799+50.753766i | 10.798674+0.0001i |  | 0.0108+50.73079i | 0.111553+547.825264i | 10.809474+50.73089i | 10.330125+2.19889i | 10.330225+1.647468i | 47 | 10.4608
[56 empty] | 47.2 | 0.0001-0.549085i | 0.000001-0.022879i | 0.010799+50.969739i | 10.798674+0.0001i |  | 0.0108+50.94686i | 0.111531+550.158534i | 10.809474+50.94696i | 10.33392+2.19037i | 10.33402+1.641285i | 47.2 | 10.4635
[56 empty] | 47.4 | 0.0001-0.546768i | 0.000001-0.022782i | 0.010799+51.185713i | 10.798674+0.0001i |  | 0.0108+51.162931i | 0.111509+552.491814i | 10.809474+51.163031i | 10.337669+2.181913i | 10.337769+1.635145i | 47.4 | 10.4663
[56 empty] | 47.6 | 0.0001-0.544471i | 0.000001-0.022686i | 0.010799+51.401686i | 10.798674+0.0001i |  | 0.0108+51.379i | 0.111488+554.825073i | 10.809474+51.3791i | 10.341374+2.173517i | 10.341474+1.629046i | 47.6 | 10.469
[56 empty] | 47.8 | 0.0001-0.542193i | 0.000001-0.022591i | 0.010799+51.61766i | 10.798674+0.0001i |  | 0.0108+51.595069i | 0.111466+557.158331i | 10.809474+51.595169i | 10.345035+2.165182i | 10.345135+1.622989i | 47.8 | 10.4717
[56 empty] | 48 | 0.0001-0.539934i | 0.000001-0.022497i | 0.010799+51.833633i | 10.798674+0.0001i |  | 0.0108+51.811136i | 0.111445+559.491568i | 10.809474+51.811236i | 10.348654+2.156908i | 10.348754+1.616974i | 48 | 10.4743
[56 empty] | 48.2 | 0.0001-0.537693i | 0.000001-0.022404i | 0.010799+52.049607i | 10.798674+0.0001i |  | 0.0108+52.027203i | 0.111423+561.824805i | 10.809474+52.027303i | 10.352229+2.148694i | 10.352329+1.611001i | 48.2 | 10.4769
[56 empty] | 48.4 | 0.0001-0.535471i | 0.000001-0.022311i | 0.010799+52.26558i | 10.798674+0.0001i |  | 0.0108+52.243269i | 0.111401+564.158032i | 10.809474+52.243369i | 10.355763+2.140539i | 10.355863+1.605068i | 48.4 | 10.4795
[56 empty] | 48.6 | 0.0001-0.533268i | 0.000001-0.022219i | 0.010799+52.481554i | 10.798674+0.0001i |  | 0.0108+52.459335i | 0.11138+566.491258i | 10.809474+52.459435i | 10.359255+2.132442i | 10.359355+1.599174i | 48.6 | 10.4821
[56 empty] | 48.8 | 0.0001-0.531082i | 0.000001-0.022128i | 0.010799+52.697527i | 10.798674+0.0001i |  | 0.0108+52.675399i | 0.111358+568.824463i | 10.809474+52.675499i | 10.362707+2.124404i | 10.362807+1.593322i | 48.8 | 10.4846
[56 empty] | 49 | 0.0001-0.528915i | 0.000001-0.022038i | 0.010799+52.913501i | 10.798674+0.0001i |  | 0.0108+52.891463i | 0.111337+571.157667i | 10.809474+52.891563i | 10.366119+2.116424i | 10.366219+1.587509i | 49 | 10.4871
[56 empty] | 49.2 | 0.0001-0.526765i | 0.000001-0.021949i | 0.010799+53.129474i | 10.798674+0.0001i |  | 0.0108+53.107525i | 0.111315+573.490851i | 10.809474+53.107625i | 10.369492+2.1085i | 10.369592+1.581735i | 49.2 | 10.4895
[56 empty] | 49.4 | 0.0001-0.524632i | 0.000001-0.02186i | 0.010799+53.345448i | 10.798674+0.0001i |  | 0.0108+53.323588i | 0.111293+575.824044i | 10.809474+53.323688i | 10.372825+2.100633i | 10.372925+1.576001i | 49.4 | 10.492
[56 empty] | 49.6 | 0.0001-0.522516i | 0.000001-0.021772i | 0.010799+53.561421i | 10.798674+0.0001i |  | 0.0108+53.539649i | 0.111272+578.157217i | 10.809474+53.539749i | 10.376121+2.092822i | 10.376221+1.570306i | 49.6 | 10.4944
[56 empty] | 49.8 | 0.0001-0.520418i | 0.000001-0.021684i | 0.010799+53.777395i | 10.798674+0.0001i |  | 0.0108+53.755711i | 0.11125+580.4904i | 10.809474+53.755811i | 10.379379+2.085065i | 10.379479+1.564647i | 49.8 | 10.4967
[56 empty] | 50 | 0.0001-0.518336i | 0.000001-0.021597i | 0.010799+53.993368i | 10.798674+0.0001i |  | 0.0108+53.971771i | 0.111229+582.823561i | 10.809474+53.971871i | 10.3826+2.077364i | 10.3827+1.559028i | 50 | 10.4991
1
1.414
154.3399
926.0397
9.96
[58 empty] | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13
[56 empty] | VCAP HARMONIC VOLTAGE (volts)^2 |  | 51956597.2802 | 0 | 0 | 0 | 268672.5545 | 87729.8137 | 19983.909 | 3577.0015 |  | 14.0834
[56 empty] | Filter Current (amps) (In)^2 |  | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 |  | 76.8613
[56 empty] | kvar (single phase) MAIN CAP |  | 2004.7446 | 0 | 0 | 0 | 51.8336 | 23.6954 | 8.4819 | 1.7942 |  | 3827.6923
[58 empty] | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37
[56 empty] | VCAP HARMONIC VOLTAGE (volts)^2 |  | 929.6628 | 186.0613 | 126.9719 | 107.469 | 0 | 0 | 54.8311 | 49.0637
[56 empty] | Filter Current (amps) (In)^2 |  | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100
[56 empty] | kvar (single phase) MAIN CAP |  | 0.60981 | 0.1364 | 0.11268 | 0.10367 | 0 | 0 | 0.074048 | 0.070045
Table below handles the aux capacitor, inductor and resistor for loss, voltage, and rms calculations
[56 empty] | harmonic # |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37
[56 empty] | Total filter amps |  | 278.1241 | 0 | 0 | 0 | 100 | 80 | 60 | 30 | 20 | 10 | 10 | 10 | 0 | 0 | 10 | 10
[56 empty] | Total filter amps^2 |  | 77353.0402 | 0 | 0 | 0 | 10000 | 6400 | 3600 | 900 | 400 | 100 | 100 | 100 | 0 | 0 | 100 | 100
[56 empty] | R, XL, XCA EQUIVALENT IMPEDANCE (ohms) |  | 0 | 1.6019 | 2.7824 | 3.7917 | 4.6729 | 6.107 | 7.9603 | 8.5404 | 9.2994 | 9.5502 | 9.9002 | 10.0241 | 10.2075 | 10.2762 | 10.3825 | 10.4241
[56 empty] | Voltage Across Resistor (volts) |  | 0 | 0 | 0 | 0 | 467.2922 | 488.5565 | 477.6172 | 256.2106 | 185.9887 | 95.5018 | 99.0016 | 100.241 | 0 | 0 | 103.8254 | 104.2413
[56 empty] | I REACTOR & AUX CAP (AMPS) |  | 278.1241 | 0 | 0 | 0 | 90.1523 | 65.9783 | 40.5435 | 18.3595 | 10.1665 | 4.6676 | 3.9936 | 3.719 | 0 | 0 | 2.7493 | 2.6109
[56 empty] | I RESISTOR (amps) |  | 0 | 0 | 0 | 0 | 43.2731 | 45.2423 | 44.2292 | 23.7261 | 17.2233 | 8.8438 | 9.1679 | 9.2827 | 0 | 0 | 9.6146 | 9.6532
[56 empty] | I RESISTOR^2 |  | 0 | 0 | 0 | 0 | 1872.5618 | 2046.8629 | 1956.2264 | 562.9288 | 296.6418 | 78.2136 | 84.0511 | 86.1688 | 0 | 0 | 92.4414 | 93.1834
[56 empty] | Resistor losses (kW) |  | 0 | 0 | 0 | 0 | 20.2212 | 22.1034 | 21.1247 | 6.0789 | 3.2033 | 0.8446 | 0.90764 | 0.93051 | 0 | 0 | 0.99824 | 1.0063
[56 empty] | Vcap aux Harmonic Voltage |  | 300.3372 | 0 | 0 | 0 | 19.4705 | 10.1783 | 3.9801 | 1.5251 | 0.64579 | 0.26528 | 0.1875 | 0.16064 | 0 | 0 | 0.084825 | 0.0762
[56 empty] | Vcap aux harmonic voltage^2 |  | 90202.4258 | 0 | 0 | 0 | 379.1006 | 103.597 | 15.8415 | 2.3258 | 0.41705 | 0.070375 | 0.035157 | 0.025806 | 0 | 0 | 0.0071952 | 0.0058064
[56 empty] | (I REACTOR & AUX CAP)^2 |  | 77353.0402 | 0 | 0 | 0 | 8127.4382 | 4353.1371 | 1643.7736 | 337.0712 | 103.3582 | 21.7864 | 15.9489 | 13.8312 | 0 | 0 | 7.5586 | 6.8166
[56 empty] | KVAR (SINGLE PHASE) AUX CAP |  | 83.531 | 0 | 0 | 0 | 1.7553 | 0.67154 | 0.16137 | 0.027999 | 0.0065655 | 0.0012382 | 0.00074881 | 0.00059744 | 0 | 0 | 0.00023321 | 0.00019895
[56 empty] | I2R REACTOR LOSSES |  | 835.3102 | 0 | 0 | 0 | 87.7656 | 47.0081 | 17.7506 | 3.6399 | 1.1161 | 0.23526 | 0.17223 | 0.14936 | 0 | 0 | 0.081623 | 0.073611
VLN
JXL
-JXCA
R
-JXCM
𝑄_𝑒𝑓𝑓=𝑂𝑢𝑡𝑝𝑢𝑡 𝑀𝑉𝐴𝑅 𝑅𝑎𝑡𝑖𝑛𝑔 𝑜𝑓 𝐹𝑖𝑙𝑡𝑒𝑟=(𝐷𝑒𝑠𝑖𝑟𝑒𝑑 3 𝑃ℎ𝑎𝑠𝑒 𝑘𝑣𝑎𝑟)/1000 =1.0 𝑀𝑉𝐴𝑅
k
k𝑉_𝐿𝐿𝑆𝑌𝑆=𝐹𝑖𝑙𝑡𝑒𝑟 𝑁𝑜𝑚𝑖𝑛𝑎𝑙 𝐿𝑖𝑛𝑒−𝑡𝑜−𝐿𝑖𝑛𝑒 𝑉𝑜𝑙𝑡𝑎𝑔𝑒 𝑅𝑎𝑡𝑖𝑛𝑔 (𝐾𝑉)=13.8 𝑘𝑉
(ohms) =
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/𝑄_𝑒𝑓𝑓 (ohms) = 𝑋_𝐶𝑀=〖13.8〗^2/(1.0 )=190.4 (𝑜ℎ𝑚𝑠)
=
𝑋_𝐿=𝑋_𝑒𝑓𝑓/(ℎ_𝑛^2−1) = 190.4/(〖4.7〗^2−1)=9.03 𝑜ℎ𝑚𝑠
=
𝑋_𝐶𝐴=𝑋_𝐿 = 9.03 𝑜ℎ𝑚𝑠
= 23.95 mH
𝐻(𝑖𝑛𝑑𝑢𝑐𝑡𝑎𝑛𝑐𝑒)=𝑋_𝐿/2𝜋𝑓×1000(𝑚𝐻)=9.03/(2𝜋 60)×1000(𝑚𝐻)= 23.95 mH
〖𝑄_(𝐶𝐴 𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸 (𝑀𝑉𝐴𝑅)) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶𝐴 =(0.6)^2/9.03=0.040 𝑀𝑉𝐴𝑅/𝑃ℎ𝑎𝑠𝑒〗_
〖𝑄_(𝐶𝑀 𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸 (𝑀𝑉𝐴𝑅)) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶𝑀 =(9.54)^2/190.4=0.478 𝑘𝑣𝑎𝑟/𝑃ℎ𝑎𝑠𝑒〗_
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆 )×1000=1.0/(1.73×13.8)×1000=41.88 𝑎𝑚𝑝𝑠
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒𝐼_𝑛^2 )
R
R=𝐷𝐹×𝑥_𝐿×ℎ (𝑜ℎ𝑚𝑠)
(f)
𝐶=1/(2𝜋𝑓𝑋_𝑐 ) (f)
𝐿=𝑋_𝐿/2𝜋𝑓 (𝐻)
This spreadsheet is used to support the design, tuning, and component selection associated with C-HP harmonic filters as engineered by VarStec Power Solutions. It provides a consistent methodology for determining all electrical parameters required for proper filter performance, including reactances, inductances, capacitor reactive power ratings and associated voltage ratings, harmonic currents, voltage stresses, and damping resistance. The summary below describes the calculation process applied throughout the tool. The tool assumes that harmonic simulations have been conducted and the harmonic current spectrum into the harmonic filter is known. These values are inserted in the blue highlighted fields of rows 24 and 25 on page 1. For additional information, engineering support, or custom filter designs, contact VarStec Power Solutions at info@varstec.com. The design process begins by establishing the fundamental kvar requirement of the harmonic filter, typically based on the kvar demand of the connected load or the kvar allocation assigned to each stage of a multi-stage harmonic filter system. This requirement is defined as and forms the foundation of all subsequent calculations. Using the system’s nominal line-to-line voltage , the spreadsheet determines the fundamental capacitive reactance of the main capacitor section, . For a C-HP filter, this value directly represents the main capacitor reactance, .
Tuning the filter to the specified harmonic order requires defining the reactances in the series tuning branch. The reactor’s inductive reactance at the fundamental frequency, , is computed using standard tuning relationships. In a classical C-HP topology, the auxiliary capacitor section is sized such that its capacitive reactance equals the inductive reactance of the tuning reactor, giving . This establishes a tuned L-C branch in parallel with the damping resistor (high-pass resistor) and eliminates fundamental-frequency losses in the high-pass resistor allowing for an efficient low damping factor high-pass harmonic filter. Once the tuning reactances are known, the corresponding reactor inductance is calculated directly from and the system frequency.
This spreadsheet is used to support the design, tuning, and component selection associated with C-HP harmonic filters as engineered by VarStec Power Solutions. It provides a consistent methodology for determining all electrical parameters required for proper filter performance, including reactances, inductances, capacitor reactive power ratings and associated voltage ratings, harmonic currents, voltage stresses, and damping resistance. The summary below describes the calculation process applied throughout the tool. The tool assumes that harmonic simulations have been conducted and the harmonic current spectrum into the harmonic filter is known. These values are inserted in the blue highlighted fields of rows 24 and 25 on page 1. For additional information, engineering support, or custom filter designs, contact VarStec Power Solutions at info@varstec.com. The design process begins by establishing the fundamental kvar requirement of the harmonic filter, typically based on the kvar demand of the connected load or the kvar allocation assigned to each stage of a multi-stage harmonic filter system. This requirement is defined as 𝑄_𝑒𝑓𝑓and forms the foundation of all subsequent calculations. Using the system’s nominal line-to-line voltage 𝑘𝑉_𝐿𝐿𝑆𝑌𝑆, the spreadsheet determines the fundamental capacitive reactance of the main capacitor section, 𝑋_𝑒𝑓𝑓. For a C-HP filter, this value directly represents the main capacitor reactance, 𝑋_𝐶𝑀=𝑋_𝑒𝑓𝑓.
Tuning the filter to the specified harmonic order ℎ requires defining the reactances in the series tuning branch. The reactor’s inductive reactance at the fundamental frequency, 𝑋_𝐿, is computed using standard tuning relationships. In a classical C-HP topology, the auxiliary capacitor section is sized such that its capacitive reactance equals the inductive reactance of the tuning reactor, giving 𝑋_(𝐶 𝐴𝑈𝑋)=𝑋_𝐿. This establishes a tuned L-C branch in parallel with the damping resistor (high-pass resistor) and eliminates fundamental-frequency losses in the high-pass resistor allowing for an efficient low damping factor high-pass harmonic filter. Once the tuning reactances are known, the corresponding reactor inductance 𝐿 is calculated directly from 𝑋_𝐿and the system frequency.
The harmonic filter design must ensure capacitor operating duties stay within IEEE/IEC-rated limits, including the allowable 10% continuous overvoltage. The spreadsheet checks four key parameters against their rated duty: % Rated Volts, % Crest Voltage, % Amps, % kVAR. If any value exceeds its limit, the cell turns red. In that case, increase the capacitor voltage rating. The objective is to meet the required duty without significantly exceeding the rating, which would increase cost.
Capacitor kvar ratings for both the main and auxiliary groups are then determined using their rated operating voltage. The spreadsheet next evaluates the high-pass damping resistor. Its ohmic value is derived from the specified damping factor (DF) of the C-HP filter (determined from harmonic simulations), linking the resistor to the tuning reactance at the harmonic frequency. With kvar and reactances established, the tool computes the fundamental filter current and applies injected harmonic current data to evaluate the resulting capacitor voltage stresses, current duty, and reactive power duty. These computed values are compared against industry-standard capacitor ratings to confirm suitability for the intended application.
The spreadsheet then resolves the fundamental and harmonic currents flowing in the reactor, auxiliary capacitor section, and high-pass resistor. This is performed using complex current-divider calculations to ensure accurate representation of harmonic behavior. The watt loss in the damping resistor is subsequently computed and verified against its thermal rating.
Taken together, these calculations define a complete, consistent, and repeatable VarStec methodology for the engineering of C-HP harmonic filters. The spreadsheet determines all critical design parameters, including reactances, inductance, kvar requirements, current loading, voltage stress, and damping characteristics, using standardized electrical notation to provide traceability, transparency, and field-proven reliability.

## Notch Reverse Calculator
VarStec Power Solutions, Inc.
PO Box 942
Saratoga Springs, NY 12866
518.369.7589
Notch Filter Reverse Filter Calculator Tool
November 25, 2025
📜 PURPOSE OF REVERSE CALCULATORS
VarStec uses the Notch Filter reverse filter calculator tool to back into filter designs when only inductance (L) and capacitance (C) are specified. A reverse calculator provides the more usual filter rating details to allow for a complete filter design where reactive power (kvar), tuning point (h), and system voltage (kVLLSYS) are specified.
📜 REVERSE CALCULATOR
HP Filter Reverse Calculation Using C and L
|  |  | C (Capacitance - Main Group): | 98.26 | (µf)/Phase)
|  | HL (Inductance of tuning reactor): |  | 2.86 | mH
|  |  | kVLLsys (System Line-to-Line Voltage Rating): | 12.47 | kV
|  | f (System Frequency): |  | 60 | Hz
|  |  | XL (Inductive Reactance): | 1.0782 | Ohms
|  |  | XC (capacitive Reactance, Main Group): | 26.9963 | Ohms/phase
|  |  | h (Tuning Point): | 5.0039
|  |  | Qeff(3-Phase Reactive Power Output of Filter): | 5.9997 | MVAR (3-phase)
Notch Filter One-Line
Disclaimer and Use Limitation
This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
| Info@VarStec.com | [6 empty] | Rev Date: 12-26-2025

## High-Pass Reverse Calculator
VarStec Power Solutions, Inc.
PO Box 942
Saratoga Springs, NY 12866
518.369.7589
High-Pass (HP) Reverse Filter Calculator Tool
November 25, 2025
📜 PURPOSE OF REVERSE CALCULATORS
VarStec uses the High-Pass reverse filter calculator tool to back into filter designs when only inductance (L) and capacitance (C) are specified. A reverse calculator provides the more usual filter rating details to allow for a complete filter design where reactive power (kvar), tuning point (h), and system voltage (kVLLSYS) are specified.
📜 REVERSE CALCULATOR
HP Filter Reverse Calculation Using C and L
|  |  | C (Capacitance - Main Group): | 98.26 | (µf)/Phase)
|  | HL (Inductance of tuning reactor): |  | 2.86 | mH
|  |  | R (High-Pass Resistor Resistance): | 16.2 | Ohms
|  |  | kVLLsys (System Line-to-Line Voltage Rating): | 12.47 | kV
|  | f (System Frequency): |  | 60 | Hz
|  |  | XL (Inductive Reactance): | 1.0782 | Ohms
|  |  | XC (capacitive Reactance, Main Group): | 26.9963 | Ohms/phase
|  |  | h (Tuning Point): | 5.0039
|  |  | DF (Damping Factor): | 3.0028
|  |  | Qeff(3-Phase Reactive Power Output of Filter): | 5.9997 | MVAR (3-phase)
High-Pass Filter One-Line
Disclaimer and Use Limitation
This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
| Info@VarStec.com | [6 empty] | Rev Date: 12-26-2025

## C-High-Pass Reverse Calculator
VarStec Power Solutions, Inc.
PO Box 942
Saratoga Springs, NY 12866
518.369.7589
C-High-Pass (C-HP) Reverse Filter Calculator Tool
November 25, 2025
📜 PURPOSE OF REVERSE CALCULATORS
VarStec uses the C-High-Pass reverse filter calculator tool to back into filter designs when only inductance (L) and capacitances (CAUX and CMAIN) are specified. A reverse calculator provides the more usual filter rating details to allow for a complete filter design where reactive power (kvar), tuning point (h), and system voltage (kVLLSYS) are specified.
📜 REVERSE CALCULATOR
C-HP Filter Reverse Calculation Using CAUX, CMAIN, and L
|  |  | CMAIN (Capacitance - Main Group): | 85.29 | (µf)/Phase)
|  |  | CAUX (Capacitance - Auxiliary Group): | 2047.06 | (µf)/Phase)
|  |  | R (High-Pass Resistor Resistance): | 19.44 | Ohms
|  | HL (Inductance of tuning reactor): |  | 3.44 | mH
|  |  | kVLLsys (System Line-to-Line Voltage Rating): | 12.47 | kV
|  | f (System Frequency): |  | 60 | Hz
|  |  | XL (Inductive Reactance): | 1.2968 | Ohms
|  |  | XC-MAIN (capacitive Reactance, Main Group): | 31.1017 | Ohms/phase
|  |  | XC-AUX (Capacitive Reactance, Aux Group): | 1.2958 | Ohms/phase
|  |  | h (Tuning Point): | 4.9982
|  |  | DF (Damping Factor): | 2.9992
|  |  | Qeff(3-Phase Reactive Power Output of Filter): | 4.9999 | MVAR (3-phase)
C-High-Pass Filter One-Line
Disclaimer and Use Limitation
This spreadsheet is provided for preliminary engineering evaluation only. The calculations are based on simplified, steady-state models and user-supplied input data and are intended to support initial screening, comparative analysis, and conceptual design. It is intended for use only by qualified technical professionals and should not be used as a substitute for detailed engineering studies, manufacturer-validated analyses, or final design verification. VarStec Power Solutions, LLC makes no representations or warranties, express or implied, and assumes no responsibility or liability for decisions or actions taken based on use of this tool.
| Info@VarStec.com | [6 empty] | Rev Date: 12-26-2025